## Themes (hidden)
NHS Themes | Concept | Approach | Impact | Measures ….yet to be defined
Climate Change | Delivery of a sustainable estate that effectively manages climate related risk. | Buildings and resources continue to meet operational needs without undermining the integrity and stability of natural systems. Resilience measures to absorb stresses and maintain function in the face of the external pressures imposed by climate change. Adapt and evolve to better prepare for future climate change impacts. | Environmental benefit Carbon reduction Resilience Security of supply Operational efficiencies Economic benefit | Anticipation, preparation, planning Sustainable development Future proofing Risk management Mitigation Adaptation Resilience
Wellbeing | Design, management and operation of an estate that is considerate to physical, mental and social wellbeing. | Design that prioritises the wellbeing of users through the creation of comfortable, inclusive and healthy places. | Social benefit User wellness Productivity Retention Economic benefit | A state of complete physical, mental and social wellbeing. Safety /Considerate /Wellness / Quality / Connected / Happy
Circularity | Establishing an economic system that is aimed at eliminating waste and the continuous use of resources. | A framework for an economy that is restorative and regenerative by design. Based on 3 principles: - Design out waste and pollution - Keep products and materials in use - Regenerate natural systems | Environmental benefit Carbon reduction Reduced waste Maintenance efficiencies Economic benefit | A circular economy is an alternative to a traditional linear economy (make, use, dispose) in which we keep resources in use for as long as possible, extract the maximum value from them whilst in use, then recover and regenerate products and materials at the end of each service life.

## BREEAM NSAT Mapping (hidden)
BREEAM NC UK 2018 Standard | [8 empty] | Aim alignment |  |  | NSAT 2019 |  |  | Notes
Category | Issue |  | Aim | Weight. | Credits | Innovation | Minimum standards |  | Climate Change | Wellbeing | Circularity | Category | Issue | Indicator
Management | Man 01 | Project brief and design | To optimise final building design through recognising and encouraging an integrated design process and robust stakeholder engagement. | 11% | 4 | [6 empty] | Capital Projects | CP4 | We have a set of clear sustainability aims and objectives that are scaled and applied to all capital projects and major refurbishment
[12 empty] | Capital Projects | CP18 | Our new buildings and major refurbishments achieve the equivalent of BREEAM healthcare excellent or very good respectively, and the equivalent percentage is agreed with Health Facilities Scotland through the National Design Assessment Process (NDAP)
[12 empty] | Capital Projects | CP1 | We have a sustainable capital projects plan which ensures all potential opportunities in new builds and major refurbishments are leveraged for sustainability benefit, including climate change
[12 empty] | Capital Projects | CP14 | Community Benefit outcomes are embedded into the brief, design, construction and operation of capital projects
| Man 02 | Life cycle cost and service life planning | To promote the business case for sustainable buildings and to deliver whole life value by encouraging the use of life cycle costing to improve design, specification, through-life maintenance and operation. |  | 4 | [6 empty] | Capital Projects | CP6 | We apply whole life costing to capital projects to ensure that health, sustainability and value for money objectives are realised in the design and build process
[12 empty] | Procurement | P2 | Whole life costing and life cycle impact mapping are a core part of all our Board's procurements | Cross-over with Mat01
| Man 03 | Responsible construction practices | To recognise and encourage construction sites which are managed in an environmentally and socially considerate, responsible and accountable manner. |  | 6 | 1% | Outstanding (2) Excellent (1) | responsible construction management |  |  |  | Procurement | P7 | We monitor the environmental impacts (CO2e and air pollution) associated with our suppliers' transport and logistics and are actively working with our suppliers to find ways to minimise their traffic burden
| Man 04 | Commissioning and handover | To encourage a properly planned handover and commissioning process that reflects the needs of the building occupants. |  | 4 |  | Outstanding (1) Excellent (1) Very Good (1) | commissioning-test schedule and responsibilities Building User Guide |  |  |  | Capital Projects | CP7 | We appoint a commissioning manager early in the design development, to establish clear commissioning and handover protocols (e.g. ≥3 yr 'soft landings') to ensure the facility is safe for use on delivery and achieves optimal performance on occupation
[12 empty] | Capital Projects | CP15 | On occupation of a new building we communicate with and induct staff on the way it works and support them to make energy efficiency decisions aligned to the BMS/controls and design strategy
| Man 05 | Aftercare | To ensure the building operates in accordance with the design intent and operational demands, through providing aftercare to the building owner and occupants during the first year of occupation. | [8 empty] | Capital Projects | CP8 | Within commissioning and handover processes we monitor and report on the in-use performance of our new building and refurbishment projects to ensure they meet our design objectives and aspirations
[12 empty] | Capital Projects | CP16 | Following completion, we carry out post project evaluation and post occupancy surveys, including health, sustainability and other outcome monitoring
[12 empty] | Capital Projects | CP17 | After occupancy we assess energy performance of the building in-use to ensure the parameters set in the design process have been achieved and work with the contractor to rectify any areas of poor performance
[5 empty] | 3 |  | Outstanding (1) Excellent (1) | Commission - implementation |  |  |  | Greenhouse Gases | G7 | We measure, at least annually, our greenhouse gas impact for all all core emissions sources and analyse trends over time to help validate performance and ensure lessons are learned
[12 empty] | Awareness | A2 | We have a clear communications plan around the promotion of sustainability
[12 empty] | Awareness | A4 | We clearly communicate to staff and patients the value we place on becoming a net zero carbon organisation due to the adverse effects of climate change on human health
Health and Wellbeing | Hea 01 | Visual comfort | To encourage best practice in visual performance and comfort by ensuring daylighting, artificial lighting and occupant controls are considered. | 14% | 6 | 2% | [5 empty] | Welfare | W4 | We can demonstrate that our workforce strategy is having positive impacts on health, wellbeing and sustainability
| Hea 02 | Indoor air quality | To encourage and support healthy internal environments with good indoor air quality. |  | 4 | 1% | [5 empty] | Welfare | W5 | We can demonstrate that we are taking action to improve the health and wellbeing of our workforce in line with Scottish Government policy
| Hea 04 | Thermal comfort | To ensure the building is capable of providing an appropriate level of thermal comfort. |  | 3 | [6 empty] | Capital Projects | CP11 | Our capital projects and major refurbishments are designed to be usable during future projected weather profiles
[12 empty] | Adaptation | AD3 | We have programme of monitoring to capture data that will enable a robust assessment of the nature and severity of overheating at selected in-patient facilities
| Hea 05 | Acoustic performance | To ensure the building is capable of providing an appropriate acoustic environment to provide comfort for building users. |  | 3
| Hea 06 | Security | To encourage the planning and implementation of effective measures that provide an appropriate level of security to the building and site. |  | 1 | 1%
| Hea 07 | Safe and healthy surroundings | To encourage the provision of safe access around the site and outdoor space that enhances the wellbeing of building users. | [8 empty] | Capital Projects | CP12 | We design new facilities and external public spaces that promote equality and healthy choices
[5 empty] | 2 | [6 empty] | Greenspace | G5 | There is open access to high quality well maintained green spaces on our estate for the use of local residents and the wider community
Energy | Ene 01 | Reduction of energy use and carbon emissions | To minimise operational energy demand, primary energy consumption and CO₂ emissions. | 16% | 13 | 5% | Outstanding (6) Excellent (4) | Energy performance or Prediction of operational energy consumption |  |  |  | Sustainable Care | S10 | We have calculated the environmental impact of specific care model(s) and this has allowed us to identify the areas of greatest impact and to minimise those impacts
[12 empty] | Greenhouse Gases | GHG1 | We have set SMART greenhouse gas reduction targets with a baseline year and clear target date which are aligned with or exceed Scottish Government targets
[12 empty] | Greenhouse Gases | GHG5 | We identify and maximise greenhouse gas reduction opportunities in all investments, particularly in energy, buildings and transport
[12 empty] | Environmental management | EM2 | We have ambitious targets to reduce our energy demand and to improve energy efficiency in line with Scottish Government aspirations
[12 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Mat01, Tra01, Tra02 & Pol03
| Ene 02 | Energy monitoring | To encourage the installation of energy sub-metering to facilitate the monitoring of operational energy consumption. To enable managers and consultants post-handover to compare actual performance with targets in order to inform ongoing management and help in reducing the performance gap. | [8 empty] | Environmental Management | EM4 | We have developed and implemented systems to monitor our energy and water use closely across all of our sites (owned and leased)
[5 empty] | 2 |  | Outstanding (1) Excellent (1) Very Good (1) | First sub-metering credit |  |  |  | Environmental Management | EM5 | Across our estate we have implemented sub-metering for heat, cooling, power and water where savings may be anticipated
| Ene 03 | External lighting | To reduce energy consumption through the specification of energy efficient light fittings for external areas of the development. |  | 1
| Ene 04 | Low carbon design | To encourage the adoption of design measures, which reduce building energy consumption and associated carbon emissions and minimise reliance on active building services systems. |  | 3 | [6 empty] | Environmental Management | EM7 | We generate heating and cooling through on-site or off-site renewable and / or low carbon technologies in line with Scottish Government targets
| Ene 05 | Energy efficient cold storage | To encourage the installation of energy efficient refrigeration systems, in order to reduce operational greenhouse gas emissions resulting from the system's energy use. |  | 2
| Ene 06 | Energy efficient transportation systems | To encourage the specification of energy efficient transportation systems within buildings. |  | 3
| Ene 07 | Energy efficient laboratory systems | To encourage laboratory areas that are designed to minimise their operational energy consumption and associated CO₂ emissions. |  | 5
| Ene 08 | Energy efficient equipment | To encourage installation of energy efficient equipment to ensure optimum performance and energy savings in operation. |  | 2
Transport | Tra 01 | Transport assessment and travel plan | To reward awareness of existing local transport and identify improvements to make it more sustainable. | 10% | 2 | [6 empty] | Transport | T10 | Where required (either in planning or due to travel issues) we create site Green Travel Plans to make better use of our transport options
[12 empty] | Governance & Policy | G10 | We have a Sustainable Travel Strategy for our estate to encourage active travel and the use of public transport
[12 empty] | Governance & Policy | G11 | We have a travel policy that states where business travel is unavoidable we apply a travel hierarchy, promoting active travel, public transport, car sharing and low carbon vehicles before single occupancy standard vehicles
[12 empty] | Active Travel | AT6 | We carry out an annual travel survey to monitor the travel choices of our staff, patients, visitors and suppliers and measure shifts in modes of transport
[12 empty] | Active Travel | AT7 | We provide detailed information to patients and visitors on how to avoid using a car when accessing our sites
[12 empty] | Active Travel | AT8 | We actively promote the health, environmental and cost benefits of walking and cycling to our staff, patients and visitors
[12 empty] | Communities | WC6 | We have measured the impact of our travel and transport in environmental, financial and health terms and taken action to reduce traffic and associated air quality impacts in our local area
[12 empty] | Active Travel | AT2 | We have an ambitious target to increase the number of everyday staff journeys made by bike
[12 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Mat01, Ene01, Tra02 & Pol03
| Tra 02 | Sustainable transport measures | To maximise the potential for local public, private and active transport through provision of sustainable transport measures appropriate to the site. | [8 empty] | Capital Projects | CP13 | We provide facilities at our sites to encourage physical activity and active travel which are accessible to staff and visitors alike
[12 empty] | Active Travel | AT3 | We provide facilities at our sites to encourage active travel which are accessible to staff and visitors alike
[12 empty] | Active Travel | AT5 | We work in partnership to increase both the provision and connectivity of active travel infrastructure across our estate
[5 empty] | 10 | [6 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Mat01, Ene01, Tra01 & Pol03
Water | Wat 01 | Water consumption | To reduce the consumption of potable water for sanitary use in new buildings through the use of water efficient components and water recycling systems. | 7% | 5 | 1% | Outstanding (2) Excellent (1) Very Good (1) Good (1) | Efficient component specification.
| Wat 02 | Water monitoring | To reduce the consumption of potable water in new buildings through the effective management and monitoring of water consumption. | [8 empty] | Environmental Management | EM4 | We have developed and implemented systems to monitor our energy and water use closely across all of our sites (owned and leased) | Cross-over with Ene02
[5 empty] | 1 |  | Outstanding Excellent Very Good Good | Water meter specified on the mains water supply. |  |  |  | Environmental Management | EM5 | Across our estate we have implemented sub-metering for heat, cooling, power and water where savings may be anticipated
| Wat 03 | Water leak detection | To reduce the consumption of potable water in new buildings through minimising wastage due to water leaks. |  | 2
| Wat 04 | Water efficient equipment | To reduce water consumption for uses not assessed under Wat 01 by encouraging specification of water efficient equipment. |  | 1
Materials | Mat 01 | Environmental impacts from construction products - Building life cycle assessment (LCA) | To reduce the burden on the environment from construction products by recognising and encouraging measures to optimise construction product consumption efficiency and the selection of products with a low environmental impact (including embodied carbon), over the life cycle of the building. | 15% | 7 | 3% | Core building services options appraisal during Concept Design LCA and LCC alignment Third party verification |  |  |  |  | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat02, Mat06, Wst01 & Wst06
[12 empty] | Procurement | P2 | Whole life costing and life cycle impact mapping are a core part of all our Board's procurements | Cross-over with Man02
[12 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Ene01, Tra01, Tra02 & Pol03
| Mat 02 | Environmental impacts from construction products - Environmental Product Declarations (EPD) | To encourage availability of robust and comparable data on the impacts of construction products through the provision of EPD. |  | 1 | [6 empty] | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat06, Wst01 & Wst06
[12 empty] | Procurement | P4 | We encourage our suppliers to exceed government guidelines for sustainability and seek to influence national contracts in this regard | Cross-over with Mat03
| Mat 03 | Responsible sourcing of construction products | To facilitate the selection of products that involve lower levels of negative environmental, economic and social impact across their supply chain including extraction, processing and manufacture. |  | 4 | 1% | Outstanding Excellent Very Good Good Pass | Legal and sustainable timber |  |  |  | Governance & Policy | G15 | We have a Sustainable Procurement Policy which describes our ambition and approaches to embed sustainability within our supply chain
[12 empty] | Procurement | P1 | We adopt a proactive approach to identifying sustainability (environmental, social and economic) opportunities and impacts in procurement and supplier management and take action to minimise sustainability risks
[12 empty] | Procurement | P4 | We encourage our suppliers to exceed government guidelines for sustainability and seek to influence national contracts in this regard | Cross-over with Mat02
[12 empty] | Procurement | P8 | We take a "better safe than sorry" approach during the procurement of hazardous substances and chemicals, eliminating suspected hazards and switching to safer alternatives
| Mat 05 | Designing for durability and resilience | To reduce the need to repair and replace materials resulting from damage to exposed elements of the building and landscape. |  | 1 | [6 empty] | Capital Projects | CP9 | Our buildings and major refurbishments are designed to allow short-term and long-term flexibility to adapt, convert, and expand
[12 empty] | Adaptation | AD1 | We have undertaken a Climate Change Risk Assessment (CCRA) to highlight risks to business continuity and resilience of supply
[12 empty] | Adaptation | AD9 | We have implemented innovative/new technologies that improve the resilience, flexibility and adaptation of our systems and infrastructure
[12 empty] | Adaptation | AD10 | We risk assess the impact of our adaptation decisions on local communities
[12 empty] | Governance & Policy | G14 | We have an Adaptation Plan, informed by a Climate Change Risk Assessment, to help mitigate the risks and reduce the likely impacts of unavoidable climate change | Climate Change Risk Assessment & Adaptation Planning tool available from HFS
| Mat 06 | Material efficiency | To avoid unnecessary materials use arising from over specification without compromising structural stability, durability or the service life of the building. |  | 1 | [6 empty] | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat02, Wst01 & Wst06
Waste | Wst 01 | Construction waste management | To reduce construction waste by encouraging reuse, recovery and best practice waste management practices to minimise waste going to landfill. | 6% | 5 | 1% | Outstanding (1) | Construction Waste Management |  |  |  | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat02, Mat06 & Wst06
| Wst 02 | Use of recycled and sustainably sourced aggregates | To encourage the use of more sustainably sourced aggregates, encourage reuse where appropriate and avoid waste and pollution arising from disposal of demolition and other forms of waste. |  | 1 | 1%
| Wst 03 | Operational waste | To encourage the recycling of operational waste through the provision of dedicated storage facilities and space. |  | 1 |  | Outstanding (1) Excellent (1) |  |  |  |  | Waste | WA1 | We have set SMART targets for waste reduction and increased recycling with a baseline year and clear target date aligned to or exceed Scottish Government waste reduction targets
[12 empty] | Waste | WA5 | We have initiatives in place to reduce overall material use in the products we buy and the services we deliver in line with Scottish Government Strategy
[12 empty] | Waste | WA7 | We can evidence that nutrients from organic waste (particularly food waste and green waste) are captured and recycled
| Wst 05 | Adaptation to climate change | To minimise the future need of carrying out works to adapt the building to take account of more extreme weather changes resulting from climate change and changing weather patterns. |  | 1 | 1% | [5 empty] | Communities | WC8 | We work with local stakeholders in identifying risks posed by current weather and climate change and we review the risks at least annually
| Wst 06 | Design for disassembly and adaptability | To avoid unnecessary materials use, cost and disruption arising from the need for future adaptation as a result of changing functional demands and to maximise the ability to reclaim and reuse materials at final demolition in line with the principles of a circular economy. |  | 2 | [6 empty] | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat02, Mat06 & Wst01
Land Use and Ecology | LE 01 | Site selection | To encourage the use of previously occupied or contaminated land and avoid land which has not been previously disturbed. | 13% | 2 | [6 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with Ene01, Mat01, Tra01, Tra02 & Pol03
| LE 02 | Ecological risks and opportunities | To determine the existing ecological value associated with the site, including surrounding areas, and the risks and opportunities for ecological protection and enhancement as part of the project. |  | 2 | 1%
| LE 03 | Managing impacts on ecology | To avoid, or limit as far as possible, negative ecological impacts associated with the site and surrounding areas resulting from the project. |  | 3
| LE 04 | Ecological change and enhancement | To enhance ecological value of the area associated with the site in support of local, regional and national priorities. |  | 4 | 1% | [5 empty] | Nature & Biodiversity | B1 | We have assessed the impacts of the provision of our services on local biodiversity and this has allowed us to put in place mitigating actions to reduce any adverse impacts, and identify enhancement actions to increase biodiversity value
[12 empty] | Nature & Biodiversity | B3 | We are actively working to improve the ecological value of our amenity space
[12 empty] | Nature & Biodiversity | B5 | We can evidence that biodiversity has improved due to our actions
[12 empty] | Governance & Policy | G13 | We have a Biodiversity Action Plan to conserve and enhance the biodiversity value of our estate
| LE 05 | Long term ecological management and maintenance | To secure ongoing monitoring, management and maintenance of the site and its habitats and ecological features, to ensure intended outcomes are realised for the long term. | [8 empty] | Governance & Policy | G12 | We have a Greenspace Strategy for our estate which provides a framework for action to help us maximise our greenspace resource
[5 empty] | 2 | [6 empty] | Nature & Biodiversity | B4 | Our grounds and green spaces are maintained in a way that minimises negative impacts and increases biodiversity value
Pollution | Pol 01 | Impact of refrigerants | To reduce the level of greenhouse gas emissions arising from the leakage of refrigerants from building systems. | 8% | 3
| Pol 02 | Local air quality | To contribute to a reduction in local air pollution through the use of low emission combustion appliances in the building. |  | 2 | [6 empty] | Greenhouse Gases | GHG5 | We identify and maximise greenhouse gas reduction opportunities in all investments, particularly in energy, buildings and transport
| Pol 03 | Flood and surface water management | To avoid, reduce and delay the discharge of rainfall to public sewers and watercourses, thereby minimising the risk and impact of localised flooding on-site and off-site, watercourse pollution and other environmental damage. | [8 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE1, Ene01, Mat01, Tra01 & Tra02
[5 empty] | 5 | [6 empty] | Adaptation | AD2 | We have assessed the risk of flooding for all of our sites, key transport/access routes, supporting infrastructure and workforce based on current and future projected climate conditions
| Pol 04 | Reduction of night time light pollution | To ensure that external lighting is concentrated in the appropriate areas and that upward lighting is minimised, thereby reducing unnecessary light pollution, energy consumption and nuisance to neighbouring properties. |  | 1
| Pol 05 | Reduction of noise pollution | To reduce the likelihood of noise arising from fixed installations on the new development affecting nearby noise sensitive buildings. |  | 1
Innovation | Inn 01 | Innovation | To support innovation within the construction industry through the recognition of sustainability-related benefits which are not rewarded by standard BREEAM issues. | 10% | 1 | 10% |  | Up to 10% can be achieved through innovation credits |  |  |  | Environmental Management | EM6 | We encourage innovation and support new technologies that help reduce energy and water use
[16 empty] | G23 & G24 | BIU
T3 & T4 & T5
B6
AT1

## Climate Change (hidden)
BREEAM NC UK 2018 Standard | [9 empty] | Aim alignment |  |  | NSAT 2019 |  |  | Notes
Category | Issue |  | Aim | Requirements | Weight. | Credits | Innovation | Minimum standards |  | Climate Change | Wellbeing | Circularity | Category | Issue | Indicator
Management | Man 01 | Project brief and design | To optimise final building design through recognising and encouraging an integrated design process and robust stakeholder engagement. | Prior to the completion of Concept Design, project delivery stakeholders meet to agree roles, responsibilities and contributions. This includes consideration of operational energy. Independent stakeholder consultation exercise is completed and outcomes influence the Initial Project Brief and Concept Design. Project team, including the client, formally agree strategic performance targets early in the design process. A suitably qualified individual guides the project through the design and construction stages. | 11% | 4 | [6 empty] | Capital Projects | CP4 | We have a set of clear sustainability aims and objectives that are scaled and applied to all capital projects and major refurbishment
[13 empty] | Capital Projects | CP18 | Our new buildings and major refurbishments achieve the equivalent of BREEAM healthcare excellent or very good respectively, and the equivalent percentage is agreed with Health Facilities Scotland through the National Design Assessment Process (NDAP)
[13 empty] | Capital Projects | CP1 | We have a sustainable capital projects plan which ensures all potential opportunities in new builds and major refurbishments are leveraged for sustainability benefit, including climate change
[13 empty] | Capital Projects | CP14 | Community Benefit outcomes are embedded into the brief, design, construction and operation of capital projects
| Man 03 | Responsible construction practices | To recognise and encourage construction sites which are managed in an environmentally and socially considerate, responsible and accountable manner. | Principle contractor operates EMS. Legal and sustainable procurement of timber. Considerate and responsible site management. Monitoring of construction site impacts. |  | 6 | 1% | Outstanding (2) Excellent (1) | responsible construction management |  |  |  | Procurement | P7 | We monitor the environmental impacts (CO2e and air pollution) associated with our suppliers' transport and logistics and are actively working with our suppliers to find ways to minimise their traffic burden
| Man 04 | Commissioning and handover | To encourage a properly planned handover and commissioning process that reflects the needs of the building occupants. | Schedule of commissioning and testing prepared. Team member appointed to monitor and programme all pre-commissioning, commissioning and testing and re-commissioning where necessary on behalf of client. Principle contractor allows time and budget to support this task. Specialist commissioning agent appointed to manage complex buildings. Building fabric inspected and tested. Building occupier and FM user guides issued prior to handover. |  | 4 |  | Outstanding (1) Excellent (1) Very Good (1) | commissioning-test schedule and responsibilities Building User Guide |  |  |  | Capital Projects | CP7 | We appoint a commissioning manager early in the design development, to establish clear commissioning and handover protocols (e.g. ≥3 yr 'soft landings') to ensure the facility is safe for use on delivery and achieves optimal performance on occupation
[13 empty] | Capital Projects | CP15 | On occupation of a new building we communicate with and induct staff on the way it works and support them to make energy efficiency decisions aligned to the BMS/controls and design strategy
| Man 05 | Aftercare | To ensure the building operates in accordance with the design intent and operational demands, through providing aftercare to the building owner and occupants during the first year of occupation. | Provision of aftercare support for a period of at least 12 months. Seasonal commissioning programme delivered. POE delivered by independent party. | [8 empty] | Capital Projects | CP8 | Within commissioning and handover processes we monitor and report on the in-use performance of our new building and refurbishment projects to ensure they meet our design objectives and aspirations
[13 empty] | Capital Projects | CP16 | Following completion, we carry out post project evaluation and post occupancy surveys, including health, sustainability and other outcome monitoring
[13 empty] | Capital Projects | CP17 | After occupancy we assess energy performance of the building in-use to ensure the parameters set in the design process have been achieved and work with the contractor to rectify any areas of poor performance
[6 empty] | 3 |  | Outstanding (1) Excellent (1) | Commission - implementation |  |  |  | Greenhouse Gases | G7 | We measure, at least annually, our greenhouse gas impact for all core emissions sources and analyse trends over time to help validate performance and ensure lessons are learned
[13 empty] | Awareness | A2 | We have a clear communications plan around the promotion of sustainability
[13 empty] | Awareness | A4 | We clearly communicate to staff and patients the value we place on becoming a net zero carbon organisation due to the adverse effects of climate change on human health
Energy | Ene 01 | Reduction of energy use and carbon emissions | To minimise operational energy demand, primary energy consumption and CO₂ emissions. | Operational energy performance improvement better than building regulations requirement. Prediction of operational energy consumption completed during design stage. | 16% | 13 | 5% | Outstanding (6) Excellent (4) | Energy performance or Prediction of operational energy consumption |  |  |  | Sustainable Care | S10 | We have calculated the environmental impact of specific care model(s) and this has allowed us to identify the areas of greatest impact and to minimise those impacts
[13 empty] | Greenhouse Gases | GHG1 | We have set SMART greenhouse gas reduction targets with a baseline year and clear target date which are aligned with or exceed Scottish Government targets
[13 empty] | Greenhouse Gases | GHG5 | We identify and maximise greenhouse gas reduction opportunities in all investments, particularly in energy, buildings and transport
[13 empty] | Environmental management | EM2 | We have ambitious targets to reduce our energy demand and to improve energy efficiency in line with Scottish Government aspirations
[13 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Mat01, Tra01, Tra02 & Pol03
| Ene 02 | Energy monitoring | To encourage the installation of energy sub-metering to facilitate the monitoring of operational energy consumption. To enable managers and consultants post-handover to compare actual performance with targets in order to inform ongoing management and help in reducing the performance gap. | Install energy metering systems so that at least 90% of the estimated annual energy consumption of each fuel is assigned to the end-use categories. Install energy sub-metering for high energy load and tenancy areas. | [8 empty] | Environmental Management | EM4 | We have developed and implemented systems to monitor our energy and water use closely across all of our sites (owned and leased)
[6 empty] | 2 |  | Outstanding (1) Excellent (1) Very Good (1) | First sub-metering credit |  |  |  | Environmental Management | EM5 | Across our estate we have implemented sub-metering for heat, cooling, power and water where savings may be anticipated
| Ene 03 | External lighting | To reduce energy consumption through the specification of energy efficient light fittings for external areas of the development. | All external light fittings within the construction zone to have average initial luminous efficacy of not less than 70 luminaire lumens per circuit Watt, Automatic control to prevent operation during daylight hours and presence detection in areas of intermittent traffic. |  | 1
| Ene 04 | Low carbon design | To encourage the adoption of design measures, which reduce building energy consumption and associated carbon emissions and minimise reliance on active building services systems. | Passive design analysis delivered during Concept Design stage. This also includes a free cooling analysis. Energy specialise delivers a LZCT feasibility study. |  | 3 | [6 empty] | Environmental Management | EM7 | We generate heating and cooling through on-site or off-site renewable and / or low carbon technologies in line with Scottish Government targets
| Ene 05 | Energy efficient cold storage | To encourage the installation of energy efficient refrigeration systems, in order to reduce operational greenhouse gas emissions resulting from the system's energy use. | Refrigeration systems in accordance with Code of Conduct for carbon reduction in the refrigeration retail sector BS EN 378-2:2016. Using robust and tested refrigeration systems or components included on ECA ETPL. Demonstrate a saving in indirect greenhouse gas emissions. |  | 2
| Ene 06 | Energy efficient transportation systems | To encourage the specification of energy efficient transportation systems within buildings. | Analyse the transportation demand and usage patterns for the building Calculate the energy consumption in accordance with BS EN ISO 25745 Part 2 or Part 3. Specify energy efficient features. |  | 3
| Ene 07 | Energy efficient laboratory systems | To encourage laboratory areas that are designed to minimise their operational energy consumption and associated CO₂ emissions. | Client engagement to inform design specification. For Labs, ave. design air flow rate is no greater than 0.16m³/s per linear metre. Specification of best practice energy efficiency measures. |  | 5
| Ene 08 | Energy efficient equipment | To encourage installation of energy efficient equipment to ensure optimum performance and energy savings in operation. | All medical equipment exempt. Procurement of large-scale equipment & sets of electrical equipment (>50) has been informed and selected by LCC analysis for at least two options in accordance with HTM07-02, Part B, Chapter 1. |  | 2
Transport | Tra 01 | Transport assessment and travel plan | To reward awareness of existing local transport and identify improvements to make it more sustainable. | Site-specific transport assessment and travel plan to be completed by end of Concept Design. Accessibility Index awards credits. Access to amenities and frequency of public transport secures a greater number of credits. | 10% | 2 | [6 empty] | Transport | T10 | Where required (either in planning or due to travel issues) we create site Green Travel Plans to make better use of our transport options
[13 empty] | Governance & Policy | G10 | We have a Sustainable Travel Strategy for our estate to encourage active travel and the use of public transport
[13 empty] | Governance & Policy | G11 | We have a travel policy that states where business travel is unavoidable we apply a travel hierarchy, promoting active travel, public transport, car sharing and low carbon vehicles before single occupancy standard vehicles
[13 empty] | Active Travel | AT6 | We carry out an annual travel survey to monitor the travel choices of our staff, patients, visitors and suppliers and measure shifts in modes of transport
[13 empty] | Active Travel | AT7 | We provide detailed information to patients and visitors on how to avoid using a car when accessing our sites
[13 empty] | Active Travel | AT8 | We actively promote the health, environmental and cost benefits of walking and cycling to our staff, patients and visitors
[13 empty] | Communities | WC6 | We have measured the impact of our travel and transport in environmental, financial and health terms and taken action to reduce traffic and associated air quality impacts in our local area
[13 empty] | Active Travel | AT2 | We have an ambitious target to increase the number of everyday staff journeys made by bike
[13 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Mat01, Ene01, Tra02 & Pol03
| Tra 02 | Sustainable transport measures | To maximise the potential for local public, private and active transport through provision of sustainable transport measures appropriate to the site. | Provision of sustainable transport measures secures credits. This can include electric vehicle charging points, cycle parking and facilities, enhanced amenities. | [8 empty] | Capital Projects | CP13 | We provide facilities at our sites to encourage physical activity and active travel which are accessible to staff and visitors alike
[13 empty] | Active Travel | AT3 | We provide facilities at our sites to encourage active travel which are accessible to staff and visitors alike
[13 empty] | Active Travel | AT5 | We work in partnership to increase both the provision and connectivity of active travel infrastructure across our estate
[6 empty] | 10 | [6 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Mat01, Ene01, Tra01 & Pol03
Water | Wat 01 | Water consumption | To reduce the consumption of potable water for sanitary use in new buildings through the use of water efficient components and water recycling systems. | Targeted water reduction through efficient specification of fixtures and fittings. Components to be included as a minimum: WCs, Wash-hand basin taps, Showers, Urinals, Kitchen taps: kitchenette Clinical areas may be omitted. | 7% | 5 | 1% | Outstanding (2) Excellent (1) Very Good (1) Good (1) | Efficient component specification.
| Wat 02 | Water monitoring | To reduce the consumption of potable water in new buildings through the effective management and monitoring of water consumption. | Specification of pulsed output water meters on the mains supply and sub-meters for high use area, including Staff and public areas, Clinical areas and wards, Letting areas: on the water supply to each tenant unit, Laundries, Main production kitchen, Hydrotherapy pools, Laboratories, Central sterile supply department (CSSD), hospital sterilisation and disinfection unit (HSDU), pathology, pharmacy, mortuary and any other major process water use, Supplementary supply of water from a cold water tank. | [8 empty] | Environmental Management | EM4 | We have developed and implemented systems to monitor our energy and water use closely across all of our sites (owned and leased) | Cross-over with Ene02
[6 empty] | 1 |  | Outstanding Excellent Very Good Good | Water meter specified on the mains water supply. |  |  |  | Environmental Management | EM5 | Across our estate we have implemented sub-metering for heat, cooling, power and water where savings may be anticipated
| Wat 03 | Water leak detection | To reduce the consumption of potable water in new buildings through minimising wastage due to water leaks. | Leak detection system that is programmable and can trigger alarm to be specified. Flow control devices specified to regulate flow to WC areas. Does not apply in clinical areas. Flow control not required for short and long term residential accommodation. |  | 2
| Wat 04 | Water efficient equipment | To reduce water consumption for uses not assessed under Wat 01 by encouraging specification of water efficient equipment. | Identify systems or processes to reduce the relevant water demand (other than those in Wat 01) and establish, through either good practice design or specification. |  | 1
Materials | Mat 01 | Environmental impacts from construction products - Building life cycle assessment (LCA) | To reduce the burden on the environment from construction products by recognising and encouraging measures to optimise construction product consumption efficiency and the selection of products with a low environmental impact (including embodied carbon), over the life cycle of the building. | There is currently no referenced benchmark for Healthcare. LCA options appraisal to be delivered during Concept Design and Technical Design stages for superstructure. Substructure and hard landscaping options appraisal during Concept Design. LCA tool must be BREEAM compliant. | 15% | 7 | 3% | Core building services options appraisal during Concept Design LCA and LCC alignment Third party verification |  |  |  |  | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat02, Mat06, Wst01 & Wst06
[13 empty] | Procurement | P2 | Whole life costing and life cycle impact mapping are a core part of all our Board's procurements | Cross-over with Man02
[13 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Ene01, Tra01, Tra02 & Pol03
| Mat 02 | Environmental impacts from construction products - Environmental Product Declarations (EPD) | To encourage availability of robust and comparable data on the impacts of construction products through the provision of EPD. | Specify construction products with EPD that achieve a total EPD points score of at least 20, credits award by using Mat 02 methodology calculation. |  | 1 | [6 empty] | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat06, Wst01 & Wst06
[13 empty] | Procurement | P4 | We encourage our suppliers to exceed government guidelines for sustainability and seek to influence national contracts in this regard | Cross-over with Mat03
| Mat 03 | Responsible sourcing of construction products | To facilitate the selection of products that involve lower levels of negative environmental, economic and social impact across their supply chain including extraction, processing and manufacture. | 100% of timber and timber-based products used on the project are 'Legal' and 'Sustainable'. A sustainable procurement plan must be used by the design team to guide specification towards sustainable construction products, must be in place before Concept Design and follow processes set out in BS ISO 20400:2017. Credits will be awarded based on volume of material that is responsibly sourced (eg FSS, BES 6001, ISO 14001). |  | 4 | 1% | Outstanding Excellent Very Good Good Pass | Legal and sustainable timber |  |  |  | Governance & Policy | G15 | We have a Sustainable Procurement Policy which describes our ambition and approaches to embed sustainability within our supply chain
[13 empty] | Procurement | P1 | We adopt a proactive approach to identifying sustainability (environmental, social and economic) opportunities and impacts in procurement and supplier management and take action to minimise sustainability risks
[13 empty] | Procurement | P4 | We encourage our suppliers to exceed government guidelines for sustainability and seek to influence national contracts in this regard | Cross-over with Mat02
[13 empty] | Procurement | P8 | We take a "better safe than sorry" approach during the procurement of hazardous substances and chemicals, eliminating suspected hazards and switching to safer alternatives
| Mat 05 | Designing for durability and resilience | To reduce the need to repair and replace materials resulting from damage to exposed elements of the building and landscape. | Protection measures are incorporated into the building's design and construction to reduce damage to the building’s fabric or materials in case of accidental or malicious damage occurring. Protection where parking or manoeuvring areas are within 1 metre of the building façade and where delivery areas or routes are within 2 metres of the façade. Potential malicious damage to building materials and finishes, in public and common areas where appropriate. Protecting exposed parts of the building from material degradation. Key exposed building elements have been designed and specified to limit long and short term degradation due to environmental factors. |  | 1 | [6 empty] | Capital Projects | CP9 | Our buildings and major refurbishments are designed to allow short-term and long-term flexibility to adapt, convert, and expand
[13 empty] | Adaptation | AD1 | We have undertaken a Climate Change Risk Assessment (CCRA) to highlight risks to business continuity and resilience of supply
[13 empty] | Adaptation | AD9 | We have implemented innovative/new technologies that improve the resilience, flexibility and adaptation of our systems and infrastructure
[13 empty] | Adaptation | AD10 | We risk assess the impact of our adaptation decisions on local communities
[13 empty] | Governance & Policy | G14 | We have an Adaptation Plan, informed by a Climate Change Risk Assessment, to help mitigate the risks and reduce the likely impacts of unavoidable climate change | Climate Change Risk Assessment & Adaptation Planning tool available from HFS
Waste | Wst 01 | Construction waste management | To reduce construction waste by encouraging reuse, recovery and best practice waste management practices to minimise waste going to landfill. | Complete a pre-demolition audit. Prepare a compliant Resource Management Plan (RMP). Specify waste reduction benchmarks. Set targets for diversion of resources from landfill. | 6% | 5 | 1% | Outstanding (1) | Construction Waste Management |  |  |  | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat02, Mat06 & Wst06
| Wst 02 | Use of recycled and sustainably sourced aggregates | To encourage the use of more sustainably sourced aggregates, encourage reuse where appropriate and avoid waste and pollution arising from disposal of demolition and other forms of waste. | Identify all potential sources of local aggregate uses and types on the project. Calculate the quantity in tonnes used. |  | 1 | 1%
| Wst 05 | Adaptation to climate change | To minimise the future need of carrying out works to adapt the building to take account of more extreme weather changes resulting from climate change and changing weather patterns. | Conduct a climate change adaptation strategy appraisal to identify the impact of expected extreme weather conditions arising from climate change on the building over its projected life cycle. |  | 1 | 1% | [5 empty] | Communities | WC8 | We work with local stakeholders in identifying risks posed by current weather and climate change and we review the risks at least annually
Land Use and Ecology | LE 01 | Site selection | To encourage the use of previously occupied or contaminated land and avoid land which has not been previously disturbed. | At least 75% of the proposed development is on previously occupied land. A contaminated land report confirms level of contamination on site and remediation action is taken. | 13% | 2 | [6 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with Ene01, Mat01, Tra01, Tra02 & Pol03
Pollution | Pol 01 | Impact of refrigerants | To reduce the level of greenhouse gas emissions arising from the leakage of refrigerants from building systems. | No refrigerant use - credits awarded by default. Electric compressors and systems with ammonia must comply with guidance. All refrigerants used have a global warming potential (GWP) ≤10. Compliant leak detection system is specified. | 8% | 3
| Pol 02 | Local air quality | To contribute to a reduction in local air pollution through the use of low emission combustion appliances in the building. | All heating and hot water is supplied by non-combustion systems OR Emissions from all installed combustion plant that provide space heating and domestic hot water do not exceed the levels set. |  | 2 | [6 empty] | Greenhouse Gases | GHG5 | We identify and maximise greenhouse gas reduction opportunities in all investments, particularly in energy, buildings and transport
| Pol 03 | Flood and surface water management | To avoid, reduce and delay the discharge of rainfall to public sewers and watercourses, thereby minimising the risk and impact of localised flooding on-site and off-site, watercourse pollution and other environmental damage. | Flood Risk Assessment confirms that flood risk for site. Low flood risk awards maximum credits. Surface water run-off rates and attenuation measures required to be considered. Procedures for mitigating and managing watercourse pollution in place. | [8 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE1, Ene01, Mat01, Tra01 & Tra02
[6 empty] | 5 | [6 empty] | Adaptation | AD2 | We have assessed the risk of flooding for all of our sites, key transport/access routes, supporting infrastructure and workforce based on current and future projected climate conditions
| Pol 04 | Reduction of night time light pollution | To ensure that external lighting is concentrated in the appropriate areas and that upward lighting is minimised, thereby reducing unnecessary light pollution, energy consumption and nuisance to neighbouring properties. | External lighting strategy has been designed in compliance with Table 2 of the Institution of Lighting Professionals (ILP) Guidance notes for the reduction of obtrusive light, 2011 and can be switched off 2300-0700. |  | 1
Innovation | Inn 01 | Innovation | To support innovation within the construction industry through the recognition of sustainability-related benefits which are not rewarded by standard BREEAM issues. | Innovation credits - must meet exemplary level performance criteria or make application to BRE Global. | 10% | 1 | 10% |  | Up to 10% can be achieved through innovation credits |  |  |  | Environmental Management | EM6 | We encourage innovation and support new technologies that help reduce energy and water use
[17 empty] | G23 & G24 | BIU
T3 & T4 & T5
B6
AT1

## Wellbeing (hidden)
BREEAM NC UK 2018 Standard | [9 empty] | Aim alignment |  |  | NSAT 2019 |  |  | Notes
Category | Issue |  | Aim | Requirements | Weight. | Credits | Innovation | Minimum standards |  | Climate Change | Wellbeing | Circularity | Category | Issue | Indicator
Management | Man 04 | Commissioning and handover | To encourage a properly planned handover and commissioning process that reflects the needs of the building occupants. | Schedule of commissioning and testing prepared. Team member appointed to monitor and programme all pre-commissioning, commissioning and testing and re-commissioning where necessary on behalf of client. Principle contractor allows time and budget to support this task. Specialist commissioning agent appointed to manage complex buildings. Building fabric inspected and tested. Building occupier and FM user guides issued prior to handover. |  | 4 |  | Outstanding (1) Excellent (1) Very Good (1) | commissioning-test schedule and responsibilities Building User Guide |  |  |  | Capital Projects | CP7 | We appoint a commissioning manager early in the design development, to establish clear commissioning and handover protocols (e.g. ≥3 yr 'soft landings') to ensure the facility is safe for use on delivery and achieves optimal performance on occupation
[13 empty] | Capital Projects | CP15 | On occupation of a new building we communicate with and induct staff on the way it works and support them to make energy efficiency decisions aligned to the BMS/controls and design strategy
| Man 05 | Aftercare | To ensure the building operates in accordance with the design intent and operational demands, through providing aftercare to the building owner and occupants during the first year of occupation. | Provision of aftercare support for a period of at least 12 months. Seasonal commissioning programme delivered. POE delivered by independent party. | [8 empty] | Capital Projects | CP8 | Within commissioning and handover processes we monitor and report on the in-use performance of our new building and refurbishment projects to ensure they meet our design objectives and aspirations
[13 empty] | Capital Projects | CP16 | Following completion, we carry out post project evaluation and post occupancy surveys, including health, sustainability and other outcome monitoring
[13 empty] | Capital Projects | CP17 | After occupancy we assess energy performance of the building in-use to ensure the parameters set in the design process have been achieved and work with the contractor to rectify any areas of poor performance
[6 empty] | 3 |  | Outstanding (1) Excellent (1) | Commission - implementation |  |  |  | Greenhouse Gases | G7 | We measure, at least annually, our greenhouse gas impact for all core emissions sources and analyse trends over time to help validate performance and ensure lessons are learned
[13 empty] | Awareness | A2 | We have a clear communications plan around the promotion of sustainability
[13 empty] | Awareness | A4 | We clearly communicate to staff and patients the value we place on becoming a net zero carbon organisation due to the adverse effects of climate change on human health
Health and Wellbeing | Hea 01 | Visual comfort | To encourage best practice in visual performance and comfort by ensuring daylighting, artificial lighting and occupant controls are considered. | Glare control strategy adopted. Ave. daylight factor of 2% achieved in staff & public areas & 3% achieved in occupied patient areas & consulting rooms, uniformity ratio of at least 0.3. Ave. & minimum daylight illuminance levels achieved. 95% of relevant spaces have adequate view out. Compliance with SLL Code for Lighting & appropriate sections of CIBSE Lighting Guide 7 for internal lighting. Compliance with BS 5489-1:2013 and BS EN 12464-2:2014 for external lighting. Internal lighting is zoned to allow for adequate occupant control. Lighting to be in accordance with CIBSE Lighting Guide 5 for teaching, seminar or lecture areas. | 14% | 6 | 2% | [5 empty] | Welfare | W4 | We can demonstrate that our workforce strategy is having positive impacts on health, wellbeing and sustainability
| Hea 02 | Indoor air quality | To encourage and support healthy internal environments with good indoor air quality. | A site-specific indoor air quality plan has been produced and implemented. The building has been designed to minimise the indoor concentration and recirculation of pollutants, HVAC systems in accordance with BS EN 16798-3:2017 and filters achieve at least SUP 2. Areas with large or variable occupancy patterns have carbon dioxide sensors installed to adjust provision. Naturally vented and mixed mode to be in accordance with CIBSE AM10. Harmful emissions from construction products minimised through specification of emission limits and testing requirements (TVOCs, formaldehydes and carcinogens). Post-construction indoor air quality testing carried to confirm compliance. |  | 4 | 1% | [5 empty] | Welfare | W5 | We can demonstrate that we are taking action to improve the health and wellbeing of our workforce in line with Scottish Government policy
| Hea 04 | Thermal comfort | To ensure the building is capable of providing an appropriate level of thermal comfort. | Thermal modelling carried out in accordance with CIBSE AM11 at detailed design stage. Full thermal analysis undertaken. Building is designed to take account of future thermal comfort needs and can adapt as required. Thermal modelling analysis informs the temperature control strategy and the proposed heating and cooling strategies to meet user needs. |  | 3 | [6 empty] | Capital Projects | CP11 | Our capital projects and major refurbishments are designed to be usable during future projected weather profiles
[13 empty] | Adaptation | AD3 | We have programme of monitoring to capture data that will enable a robust assessment of the nature and severity of overheating at selected in-patient facilities
| Hea 05 | Acoustic performance | To ensure the building is capable of providing an appropriate acoustic environment to provide comfort for building users. | Building meets the appropriate acoustic performance standards and testing requirements Sound insulation, Indoor ambient noise level and room acoustics. Compliance with Section 2 of HTM 08-01: Acoustic design requirements, 2013. A programme of pre-completion acoustic testing is carried out in accordance with the requirements of Section 7 of HTM 08-01. |  | 3
| Hea 06 | Security | To encourage the planning and implementation of effective measures that provide an appropriate level of security to the building and site. | A Suitably Qualified Security Specialist conducts an evidence-based Security needs assessment during or prior to Concept Design to inform the design of the building and development. |  | 1 | 1%
| Hea 07 | Safe and healthy surroundings | To encourage the provision of safe access around the site and outdoor space that enhances the wellbeing of building users. | Provision of dedicated safe pedestrian and cycle access to, from and within the site. vehicle delivery access and drop-off areas do not cross or compromise pedestrian or cycle routes. Appropriate separation for goods vehicles. Parking and turning areas are designed for simple manoeuvring, avoiding the need for repeated shunting. An outside space providing building users with an external amenity area. | [8 empty] | Capital Projects | CP12 | We design new facilities and external public spaces that promote equality and healthy choices
[6 empty] | 2 | [6 empty] | Greenspace | G5 | There is open access to high quality well maintained green spaces on our estate for the use of local residents and the wider community
Transport | Tra 01 | Transport assessment and travel plan | To reward awareness of existing local transport and identify improvements to make it more sustainable. | Site-specific transport assessment and travel plan to be completed by end of Concept Design. Accessibility Index awards credits. Access to amenities and frequency of public transport secures a greater number of credits. | 10% | 2 | [6 empty] | Transport | T10 | Where required (either in planning or due to travel issues) we create site Green Travel Plans to make better use of our transport options
[13 empty] | Governance & Policy | G10 | We have a Sustainable Travel Strategy for our estate to encourage active travel and the use of public transport
[13 empty] | Governance & Policy | G11 | We have a travel policy that states where business travel is unavoidable we apply a travel hierarchy, promoting active travel, public transport, car sharing and low carbon vehicles before single occupancy standard vehicles
[13 empty] | Active Travel | AT6 | We carry out an annual travel survey to monitor the travel choices of our staff, patients, visitors and suppliers and measure shifts in modes of transport
[13 empty] | Active Travel | AT7 | We provide detailed information to patients and visitors on how to avoid using a car when accessing our sites
[13 empty] | Active Travel | AT8 | We actively promote the health, environmental and cost benefits of walking and cycling to our staff, patients and visitors
[13 empty] | Communities | WC6 | We have measured the impact of our travel and transport in environmental, financial and health terms and taken action to reduce traffic and associated air quality impacts in our local area
[13 empty] | Active Travel | AT2 | We have an ambitious target to increase the number of everyday staff journeys made by bike
[13 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Mat01, Ene01, Tra02 & Pol03
| Tra 02 | Sustainable transport measures | To maximise the potential for local public, private and active transport through provision of sustainable transport measures appropriate to the site. | Provision of sustainable transport measures secures credits. This can include electric vehicle charging points, cycle parking and facilities, enhanced amenities. | [8 empty] | Capital Projects | CP13 | We provide facilities at our sites to encourage physical activity and active travel which are accessible to staff and visitors alike
[13 empty] | Active Travel | AT3 | We provide facilities at our sites to encourage active travel which are accessible to staff and visitors alike
[13 empty] | Active Travel | AT5 | We work in partnership to increase both the provision and connectivity of active travel infrastructure across our estate
[6 empty] | 10 | [6 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Mat01, Ene01, Tra01 & Pol03
Land Use and Ecology | LE 04 | Ecological change and enhancement | To enhance ecological value of the area associated with the site in support of local, regional and national priorities. | Compliance is monitored against all relevant UK, EU or international legislation relating to the ecology of the site. Measures have been implemented that enhance ecological value, which are based on input from the project team and Suitably Qualified Ecologist in collaboration with representative stakeholders and data collated as part of the ‘Determining ecological outcomes’. credits are awarded based on the change in ecological value occurring as a result of the project. |  | 4 | 1% | [5 empty] | Nature & Biodiversity | B1 | We have assessed the impacts of the provision of our services on local biodiversity and this has allowed us to put in place mitigating actions to reduce any adverse impacts, and identify enhancement actions to increase biodiversity value
[13 empty] | Nature & Biodiversity | B3 | We are actively working to improve the ecological value of our amenity space
[13 empty] | Nature & Biodiversity | B5 | We can evidence that biodiversity has improved due to our actions
[13 empty] | Governance & Policy | G13 | We have a Biodiversity Action Plan to conserve and enhance the biodiversity value of our estate
| LE 05 | Long term ecological management and maintenance | To secure ongoing monitoring, management and maintenance of the site and its habitats and ecological features, to ensure intended outcomes are realised for the long term. | Measures have been implemented to manage and maintain ecology throughout the project. A section on Ecology and Biodiversity has been included as part of the tenant or building owner information supplied, to inform the owner or occupant of local ecological features, value and biodiversity on or near the site. A Landscape and Ecology Management Plan, or equivalent, has been developed in accordance with BS 42020:2013 Section 11.1 covering at least the first five years after project completion as a minimum. Plan will be updated. | [8 empty] | Governance & Policy | G12 | We have a Greenspace Strategy for our estate which provides a framework for action to help us maximise our greenspace resource
[6 empty] | 2 | [6 empty] | Nature & Biodiversity | B4 | Our grounds and green spaces are maintained in a way that minimises negative impacts and increases biodiversity value
Pollution | Pol 02 | Local air quality | To contribute to a reduction in local air pollution through the use of low emission combustion appliances in the building. | All heating and hot water is supplied by non-combustion systems OR Emissions from all installed combustion plant that provide space heating and domestic hot water do not exceed the levels set. |  | 2 | [6 empty] | Greenhouse Gases | GHG5 | We identify and maximise greenhouse gas reduction opportunities in all investments, particularly in energy, buildings and transport
| Pol 03 | Flood and surface water management | To avoid, reduce and delay the discharge of rainfall to public sewers and watercourses, thereby minimising the risk and impact of localised flooding on-site and off-site, watercourse pollution and other environmental damage. | Flood Risk Assessment confirms that flood risk for site. Low flood risk awards maximum credits. Surface water run-off rates and attenuation measures required to be considered. Procedures for mitigating and managing watercourse pollution in place. | [8 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE1, Ene01, Mat01, Tra01 & Tra02
[6 empty] | 5 | [6 empty] | Adaptation | AD2 | We have assessed the risk of flooding for all of our sites, key transport/access routes, supporting infrastructure and workforce based on current and future projected climate conditions
| Pol 04 | Reduction of night time light pollution | To ensure that external lighting is concentrated in the appropriate areas and that upward lighting is minimised, thereby reducing unnecessary light pollution, energy consumption and nuisance to neighbouring properties. | External lighting strategy has been designed in compliance with Table 2 of the Institution of Lighting Professionals (ILP) Guidance notes for the reduction of obtrusive light, 2011 and can be switched off 2300-0700. |  | 1
| Pol 05 | Reduction of noise pollution | To reduce the likelihood of noise arising from fixed installations on the new development affecting nearby noise sensitive buildings. | no noise-sensitive areas within the assessed building or within 800 m radius OR where there are noise-sensitive areas within 800 m radius of the assessed site, a noise impact assessment compliant with BS 4142:2014 is commissioned. |  | 1
[17 empty] | G23 & G24 | BIU
T3 & T4 & T5
B6
AT1

## Circularity (hidden)
BREEAM NC UK 2018 Standard | [9 empty] | Aim alignment |  |  | NSAT 2019 |  |  | Notes
Category | Issue |  | Aim | Requirements | Weight. | Credits | Innovation | Minimum standards |  | Climate Change | Wellbeing | Circularity | Category | Issue | Indicator
Management | Man 02 | Life cycle cost and service life planning | To promote the business case for sustainable buildings and to deliver whole life value by encouraging the use of life cycle costing to improve design, specification, through-life maintenance and operation. | Competent person carries out an outline, entire asset LCC plan at Concept Design with design options appraisals in line with 'Standardised method of life cycle costing for construction procurement' PD 156865: 2008. The elemental LCC plan includes service life, maintenance and operation cost estimates. Study period to be agreed with client, default is 60 years. component level LCC completed by end of Technical Design, includes envelopes, finishes, services and external spaces. design and specification to minimise life cycle costs and maximise critical value. Report the capital cost for the building in pounds per square metre of gross internal floor area (£k/m²) as part of the submission to BRE. |  | 4 | [6 empty] | Capital Projects | CP6 | We apply whole life costing to capital projects to ensure that health, sustainability and value for money objectives are realised in the design and build process
[13 empty] | Procurement | P2 | Whole life costing and life cycle impact mapping are a core part of all our Board's procurements | Cross-over with Mat01
Materials | Mat 01 | Environmental impacts from construction products - Building life cycle assessment (LCA) | To reduce the burden on the environment from construction products by recognising and encouraging measures to optimise construction product consumption efficiency and the selection of products with a low environmental impact (including embodied carbon), over the life cycle of the building. | There is currently no referenced benchmark for Healthcare. LCA options appraisal to be delivered during Concept Design and Technical Design stages for superstructure. Substructure and hard landscaping options appraisal during Concept Design. LCA tool must be BREEAM compliant. | 15% | 7 | 3% | Core building services options appraisal during Concept Design LCA and LCC alignment Third party verification |  |  |  |  | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat02, Mat06, Wst01 & Wst06
[13 empty] | Procurement | P2 | Whole life costing and life cycle impact mapping are a core part of all our Board's procurements | Cross-over with Man02
[13 empty] | Capital Projects | CP5 | We have a process to assess the sustainability of buildings/locations when leasing or procuring based on their sustainability performance | Cross-over with LUE01, Ene01, Tra01, Tra02 & Pol03
| Mat 02 | Environmental impacts from construction products - Environmental Product Declarations (EPD) | To encourage availability of robust and comparable data on the impacts of construction products through the provision of EPD. | Specify construction products with EPD that achieve a total EPD points score of at least 20, credits award by using Mat 02 methodology calculation. |  | 1 | [6 empty] | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat06, Wst01 & Wst06
[13 empty] | Procurement | P4 | We encourage our suppliers to exceed government guidelines for sustainability and seek to influence national contracts in this regard | Cross-over with Mat03
| Mat 03 | Responsible sourcing of construction products | To facilitate the selection of products that involve lower levels of negative environmental, economic and social impact across their supply chain including extraction, processing and manufacture. | 100% of timber and timber-based products used on the project are 'Legal' and 'Sustainable'. A sustainable procurement plan must be used by the design team to guide specification towards sustainable construction products, must be in place before Concept Design and follow processes set out in BS ISO 20400:2017. Credits will be awarded based on volume of material that is responsibly sourced (eg FSS, BES 6001, ISO 14001). |  | 4 | 1% | Outstanding Excellent Very Good Good Pass | Legal and sustainable timber |  |  |  | Governance & Policy | G15 | We have a Sustainable Procurement Policy which describes our ambition and approaches to embed sustainability within our supply chain
[13 empty] | Procurement | P1 | We adopt a proactive approach to identifying sustainability (environmental, social and economic) opportunities and impacts in procurement and supplier management and take action to minimise sustainability risks
[13 empty] | Procurement | P4 | We encourage our suppliers to exceed government guidelines for sustainability and seek to influence national contracts in this regard | Cross-over with Mat02
[13 empty] | Procurement | P8 | We take a "better safe than sorry" approach during the procurement of hazardous substances and chemicals, eliminating suspected hazards and switching to safer alternatives
| Mat 05 | Designing for durability and resilience | To reduce the need to repair and replace materials resulting from damage to exposed elements of the building and landscape. | Protection measures are incorporated into the building's design and construction to reduce damage to the building’s fabric or materials in case of accidental or malicious damage occurring. Protection where parking or manoeuvring areas are within 1 metre of the building façade and where delivery areas or routes are within 2 metres of the façade. Potential malicious damage to building materials and finishes, in public and common areas where appropriate. Protecting exposed parts of the building from material degradation. Key exposed building elements have been designed and specified to limit long and short term degradation due to environmental factors. |  | 1 | [6 empty] | Capital Projects | CP9 | Our buildings and major refurbishments are designed to allow short-term and long-term flexibility to adapt, convert, and expand
[13 empty] | Adaptation | AD1 | We have undertaken a Climate Change Risk Assessment (CCRA) to highlight risks to business continuity and resilience of supply
[13 empty] | Adaptation | AD9 | We have implemented innovative/new technologies that improve the resilience, flexibility and adaptation of our systems and infrastructure
[13 empty] | Adaptation | AD10 | We risk assess the impact of our adaptation decisions on local communities
[13 empty] | Governance & Policy | G14 | We have an Adaptation Plan, informed by a Climate Change Risk Assessment, to help mitigate the risks and reduce the likely impacts of unavoidable climate change | Climate Change Risk Assessment & Adaptation Planning tool available from HFS
| Mat 06 | Material efficiency | To avoid unnecessary materials use arising from over specification without compromising structural stability, durability or the service life of the building. | At the Preparation and Brief and Concept Design stages, targets are set. Report on opportunities and methods to optimise the use of materials. Report the targets and actual material efficiencies achieved. |  | 1 | [6 empty] | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat02, Wst01 & Wst06
Waste | Wst 01 | Construction waste management | To reduce construction waste by encouraging reuse, recovery and best practice waste management practices to minimise waste going to landfill. | Complete a pre-demolition audit. Prepare a compliant Resource Management Plan (RMP). Specify waste reduction benchmarks. Set targets for diversion of resources from landfill. | 6% | 5 | 1% | Outstanding (1) | Construction Waste Management |  |  |  | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat02, Mat06 & Wst06
| Wst 02 | Use of recycled and sustainably sourced aggregates | To encourage the use of more sustainably sourced aggregates, encourage reuse where appropriate and avoid waste and pollution arising from disposal of demolition and other forms of waste. | Identify all potential sources of local aggregate uses and types on the project. Calculate the quantity in tonnes used. |  | 1 | 1%
| Wst 03 | Operational waste | To encourage the recycling of operational waste through the provision of dedicated storage facilities and space. | Dedicated space for the segregation and storage of operational recyclable waste generated. Size, waste streams (including food waste), management of large amounts of operational waste, cleaning and maintenance requirements all accounted for and designed to support operational needs and accessible to occupants. Specified or installed operational waste facilities are compliant with the relevant NHS guidelines |  | 1 |  | Outstanding (1) Excellent (1) |  |  |  |  | Waste | WA1 | We have set SMART targets for waste reduction and increased recycling with a baseline year and clear target date aligned to or exceed Scottish Government waste reduction targets
[13 empty] | Waste | WA5 | We have initiatives in place to reduce overall material use in the products we buy and the services we deliver in line with Scottish Government Strategy
[13 empty] | Waste | WA7 | We can evidence that nutrients from organic waste (particularly food waste and green waste) are captured and recycled
| Wst 05 | Adaptation to climate change | To minimise the future need of carrying out works to adapt the building to take account of more extreme weather changes resulting from climate change and changing weather patterns. | Conduct a climate change adaptation strategy appraisal to identify the impact of expected extreme weather conditions arising from climate change on the building over its projected life cycle. |  | 1 | 1% | [5 empty] | Communities | WC8 | We work with local stakeholders in identifying risks posed by current weather and climate change and we review the risks at least annually
| Wst 06 | Design for disassembly and adaptability | To avoid unnecessary materials use, cost and disruption arising from the need for future adaptation as a result of changing functional demands and to maximise the ability to reclaim and reuse materials at final demolition in line with the principles of a circular economy. | Design for disassembly and functional adaptability. Conduct a study to explore the ease of disassembly and the functional adaptation potential of different design scenarios by the end of Concept Design and develop recommendations or solutions. Update, during Technical Design. Building adaptability and disassembly guide produced to communicate the characteristics allowing functional adaptability and disassembly to prospective tenants. |  | 2 | [6 empty] | Capital Projects | CP10 | Resource efficiency and pollution prevention principles are embedded into the design and build of new facilities | Cross-over with: Mat01, Mat02, Mat06 & Wst01
[17 empty] | G23 & G24 | BIU
T3 & T4 & T5
B6
AT1

## Gap analysis (hidden)
Priority Themes | Gap Analysis
Theme | Issue | Measure | Notes
Climate Change | Whole life carbon approach | Define - net zero operational carbon target | Agree client targets and outcomes at Stage 0 | Detailed delivery approach (design - accuracy of energy simulation models and construction - build detail) - eliminating the performance gap | Guidance on renewable energy and preferred solutions - feasibility study and on-site generation | Energy models -better robustness, accuracy and details - report ave. carbon content of heat supplied | Need for client engagement throughout and review and sign-off at key stages | Design - detailed brief, inform and review simulation models, review and inform WLC and LCA reports | Construction - verification and quality assurance mechanism, lead designer involvement and direct client reporting | Handover - detailed commissioning programme and aftercare package - specialist engagement with design team (lead designer and contractor), engagement with client FM contact
|  | PLUS Best Practice approach to reduce embodied carbon - target %age reduction | Need for client engagement and early specification of performance target | Identify primary actions - pre concept design and with earlier engagement from contractor | Building Life Cycle approach | Adoption of Best Practice guidance | Post construction verification
| Fabric / material performance | Minimum performance and efficiency measures | Assurance through construction and verification in-use (overall performance) | Quality assurance and risk management at design stage - thermal performance calc and monitoring - mould / condensation / energy / health
| EUI measure | Introduction of Energy Use Intensity metric and performance indicators | Overall demand, space heating, hot water | Maximum heat loss targets | Decarbonising heat approach | Renewable electricity concepts
| In-use performance monitoring | Disclosure of data - collection, analyse, report, inform | Important step in achieving net zero carbon - verification | calibrating energy simulation models - mitigating performance gap issues & informing resilience strategies | Streamlined sector reporting | Sector transparency - data share, learning | min. 3 year POE | on-going operational environmental impacts - monitor and mitigation | Energy Waste Pollution All GHGs
Circularity | Build circular | Design and Build circular | Early stage - agree project vision - establish circular objectives | 1 Design out waste and pollution 2 Keep products and materials in use 3 Regenerate natural systems | Identify key intervention points across every stage of the building lifecycle e.g. structure and skin, services, interior spaces and settings/furniture. | Adoption of most suitable strategy - include metrics | Adoption of Best Practice guidance | Supply chain engagement | Post construction verification - analyse and impact
|  | PLUS post-construction verification | Maintenance, budgets, operational cost benefits
| Resources & Partnerships | Best Practice guidance | ZWS / Supply Chain Sustainability School | UKGBC, RICS, RIBA
|  | Resources | circular economy resources | Education for staff & sign-posting to resources
| In-use performance monitoring | Operate circular - circular business models | Management (waste, maintenance) | Operational procedures | In-use monitoring and reporting | analyse | lessons learned | Demonstrating a reduced consumption of natural resources.
|  |  | Policy and Procurement | Governance | In-use Verification | impact report | knowledge share
Wellbeing
| Healthy entrances | Design and maintenance of entrances | Pedestrian traffic, dirt, contamination etc.
| Cleanable environments | Exposed surfaces and material choices | In-use consideration - cleaning regime
| Water quality | Testing regime | In-use monitoring
| Food consumption | Strategic dining designs | Social integration | Financial wellbeing - quality and cost of food?
| Interior finishes | Colour quality and design | Design guides - different functions
| Light quality | Simulating day and night | Light quality, control, design guidance
| Circulation | Accessible, safe and visually appealing spaces | Intuitive, welcoming | Minimise travel time - complementary spaces
| Exterior design | Integration of active design elements | Physical and mental wellbeing benefit
| Active furnishings | Active workstations / standing desks | User comfort and productivity
| Ergonomics | Physical and visual | Desks, seats, computer work station designs
| Biophilic design | Bringing nature inside | Light, space, layout, features
| In-use performance monitoring | Measurement & verification | wellbeing - social, physical, mental, financial

## Themes and Issues (hidden)
Themes | Priority issues | Issue details | Metrics | Verification | Approach (to be included in guide) | 0 - POE learning | 0 | 1 | 1 | 1 or 2 | 2 | 2 | 2 | 3 | 4 | 5 | 6 | 7 | 7
Climate Change | Energy | Operational carbon | Net zero carbon and EUI benchmark | Design stage sign-off, In-use monitoring, extended POE, data disclosure | Client brief, minimum performance requirements, common energy metrics, passive design analysis, robust simulation modelling, energy monitoring and reporting strategy (meters and BMS), quality assurance through construction, detailed client engaged commissioning, standardised operational performance monitoring & planned audits , FM contracts |  | Net zero carbon commitment min. design perf. Measures Power efficiency System efficiency Heating and hot water | Utilise existing data to inform EUI benchmark (ref to CIBSE TM46??) Ref cost here for energy? | Availability of operational templates to provide accurate input data - build a data set library for NHSSS | Detailed passive design analysis | Detailed dynamic simulation modelling | Demand response | Energy strategy: Renewables Low carbon heat Storage | Review DSM before planning: -Min des perf measures -EUI -Operational assumptions -Internal environmental conditions -Metering, programme and control | Review: Approve any changes before construction Inspection - who, how and when | Quality assurance: Change control procedure Inspection reviews Physical testing | EPC - Net Zero Carbon Multi-disciplinary model (asset mngt, maintenance, in-use) FM constracts - Performance outcomes based on energy consumption - incentivsed reductoin | Model based performance analysis | Data Disclosure
| Materials | Embodied carbon | Best practice approach to embodied carbon reduction | Measurement and reporting… | Establish point of reference, performance improvement target, options appraisal, early contractor engagement, Building Life Cycle approach, post construction and in-use verification |  | Refurbish, repurpose, extension or new build. Tests fits for other possible uses (circular economy). Reuse and refurbishment in preference to demolition and new construction Fully explore the option of reuse and refurbish over new build | Adoption of consistent methodology for WLC analysis RICS methodology and IMPACT compliant LCA tool | Prioritise EPD and responsible sourcing | Comprehensive embodied carbon reduction strategy UKGBC - dev brief | WLC design analysis and options appraisals - client to build ref database from project information to act as baseline in future |  |  | Baseline carbon budget - use carbon assessments using cost plans to inform | Update carbon budget Inform tender documentation Supply chain engagement - viability assessment | Construction process - Carbon impacts monitored and reported Quality assurance: Scheduled reviews | As-built' review and final WLC assessment Carbon budget comparator Lessons learned | POE - taking account of all WLC impacts | Data Disclosure
| Water | Operational water | Water efficiency measures, management and reduction strategies | Measurement and reporting… | Specification of efficient fixtures and fittings, monitoring and controls |  | Water efficiency strategy: Reduce, harvest, recycle Monitoring, controls and leak detection |  | NHSS Water efficiency strategy: - Consumption levels: reference NHSS doc or BREEAM - Remote monitoring, controls and leak detection - Procurement: European water label scheme |  | Reducing consumption - options appraisals - harvesting of water |  |  | Client review: metering provision and consumption predictions | Full monitoring and programming integration with BMS | Quality assurance: Change control procedure - impact of specification changes | Programming of systems - client side engagement | POE - consumption monitoring, maintenance and management | Data Disclosure
| Environmental Impact | Development's impact on surrounding communities and environments | Design with nature - impact on biodiversity, green space creation / enhancement, water management strategy, impact on local air quality. | Multi design stage reviews - Measurement and reporting | Stage 0 site appraisal with multi-disciplined team input, understanding potential to unlock site value. |  | Commitment to zero negative impact | Site and strategic planning appraisals |  | Baseline sustainable landscape assessment | added value demonstrated through options appraisals | Connection with enhanced greenspace | Increase in biodiversity
| Travel and Transport | A 'Mission Zero' for transport | More sustainable transport - Provision of greener and cleaner transport choices to help deliver our net zero target. Active travel - supporting more people to make sustainable travel choices. | Measurement and reporting | Stage 0 site appraisal prioritising accessibility and safety, inclusive approach for all active and sustainable transport options, desire lines to influence concept designs, community connectivity, intuitive designs |  | Adopt a hierarchy approach that reduces the need to travel, prioritises active travel and integrates more sustainable transport options | 1 - Reducing the need to travel - digital health 2 - Shared services 3 - Integrated active travel routes 4 - Provision of more sustainable transport options | Site appraisals: Existing infrastructure - active and public transport New infrastructure - Capacity for full EV fleet (2025 and 2030 target) PLUS visitor | Site appraisal - safety, connectivity, access, security Key stakeholder engagement - LA: other complementary public sector ops | Intuitive concept designs - desire lines | [6 empty] | POE - staff, patient and visitor impact strategy impact and efficiency review | Data Disclosure
Circularity | Waste | Designing out waste and pollution | Reducing resource consumption |  | Circular approach communicated in client brief |  | disclosure of key building performance metrics prior to planning approval |  |  |  |  | Risk register and review
| Value | Value preservation | Keeping resources in use for longer |  | Building and site
| Regenerate | Regenerate natural systems | Preservation and enhancement of resources |  | Building and site
| Engagement | Behaviours and practices that support a circular economy to be increasingly mainstream | Engagement with public-facing initiatives to encourage behaviour change |  | Engagement with ZWS, CSIC, SCSSchool, Business in the Community
| Supply chain | Circular supply chains | Products designed for swap-outs, remanufacture and replacement, support supply chain development (knowledge and understanding) |  | Circular business models
Wellbeing | Physical wellness | Healthy environments | Comfortable and healthy internal environments, integration of active design elements | Design guide and multi review stages …. Final in-use monitoring and reporting | User comfort (air qual, temperature, noise, visual), physical activity spaces, exterior active design - well developed green space with purpose, interior fitness circulation, active furnishings
| Social wellness | Integration and connection with others | Designated social spaces, positive interaction | In-use monitoring and reporting | Safety and security consideration
| Mental wellness | Integrative design, visual stimulation | Biophilic design, colour quality, day / night simulation, adaptable spaces, access to enhanced external green spaces | In-use monitoring and reporting | Maintenance and management of greenspace - early stage agreement
| Occupational wellness | Enjoyment and appreciation of the work place / surroundings | Interaction, respect and ownership for surroundings | In-use monitoring and reporting | User satisfaction consultation
| Economic wellness | Access to healthy lifestyle choices | Quality, provision and affordability of healthy food and drinks, access to sustainable / active transport, access to physical activity | In-use monitoring and reporting

## Introduction
NHSScotland Sustainable Design and Construction Guidance (SDaC) SHTN 02-01 D.02
Introduction
Board Name
Project Name (ID)
General Guidance
This interactive matrix is accompanied by the NHSS Sustainable Design and Construction written guidance document and will enable users to consider all of the issues that are addressed within the guidance document. There is an interactive element to the matrix allowing users to confirm each of their project’s sustainability aspirations and achievements and offers a means of monitoring the projects progress throughout each project development stage. This matrix is designed to support self-assessment, however assessment will also be facilitated by the Property & Architecture team at all relevant and key stages.
The matrix should be at the very start of every project and updated during key review stages. Each of the four review stages are clearly highlighted within the matrix and have been scheduled to coincide with pre-planning, pre- construction, pre-occupation and during the in use (Post Occupancy Evaluation - POE) phase of the project life cycle stages. A summary of performance should be provided against each stage in the Performance Review Stages tab and it is also important to capture the person who has been assigned lead responsibility for considering each of the items listed.
The guidance is presented in such a way that it aims to correspond to the most appropriate SCIM stage / RIBA plan of work, aiming to prompt actions that will support the project in successfully realising each performance outcome.
Each of the three sustainability themes (Wellbeing, Circularity and Climate Change) and corresponding issues are listed within the matrix. Users have the option to record whether or not the project is successfully addressing each issue by recording progress against each of the action at the appropriate project stage. The following options are available for the user to select for each individual issue:
N/A - This issue is not considered applicable for this project; 0 - Consideration of this issue has not yet started for this project; 1 - Is applicable and the client and / or team are in the very early stages of considering this issue; 2 - Is applicable and the client and / or team has established an approach for addressing this issue; 3 - Is applicable and the client and / or team has broadly addressed the requirements of this issue; or 4 - Is applicable and the client and / or team has addressed all requirements of this issue, but for minor elements.
Users are expected to confirm their response within the corresponding performance review stage for each issue - this will include the presentation of required information as described within the written guidance document.
A visual performance summary has been provided on the Performance Summary tab of this document. This can be used to set aspirations for each project and track performance as each project stage develops.
The themes and corresponding issues included within the matrix are summarised below:
Wellbeing
The wellbeing theme promotes the design and operation of an estate that is considerate to and prioritises the wellbeing of users. This should be achieved through the creation of comfortable, inclusive and healthy places. These include:
W1: Healthy Places - Total Wellbeing Social, Physical, Mental, Occupational, Economic Wellbeing Place-Making Quality of Outdoor Space
W2: Indoor Environmental Quality Thermal Comfort Indoor Air Quality Air Pollutants Sound Levels Light Levels Functional Space Controls
Circularity
Issues under the circularity theme focus on establishing practices that support a more circular economy by aiming to eliminate waste and extract maximum value from resources. This includes:
CE1: Circular Design and Construction Practices Designing out Waste and Pollution Keeping Products and Materials In Use Regenerating Natural Systems Circular Procurement and Supply Chains
Climate Change
Issues under the climate change theme seek to enable the delivery of a sustainable and resilient estate that effectively manages climate and ecological risk. These include:
CC1: Operational Emissions CC2: Embodied Carbon CC3: Water Consumption CC4: Environmental Security CC5: Active Travel and Sustainable Transport
There is also an overarching theme ‘Optimising Operational Performance’. This theme aims to govern all projects delivered by all NHSS Boards and signposts to NHSS Soft Landings and Post Occupancy Evaluation requirement and it is expected that all projects will aim to address the requirements of this overarching theme. Further guidance on all themes, issues and associated actions is provided within the Guidance Document SHTN 02-01.

## Performance Review Stages
NHSScotland Sustainable Design and Construction Guidance - Performance Review Stages
Project Name (ID)
Introduction
| IA / early OBC |  | OBC |  | FBC |  | POE
Performance review stage: | Pre-Option / Site Selection / Master Planning | Performance summary | Pre-planning | Performance summary | Pre-construction | Performance summary | Handover / Post-occupation | Performance summary | Owner / Lead responsibility
Wellbeing | Update evaluation matrix to coincide with the completion of the (IA) Early OBC stage. |  | Update evaluation matrix to coincide with the completion of the Final OBC stage. |  | Update evaluation matrix and report any changes at Final FBC stage. |  | Update evaluation matrix and report any changes at pre handover stage.
W1: Healthy Places -Total wellbeing | Confirmation that Place Standard, AEDET & NDAP has been adopted. |  | Confirmation that Place Standard, AEDET & NDAP has been adopted. |  | Confirmation that stakeholder engagement has continued and feedback has influenced final design choices. |  | Place standard, AEDET & NDAP outcome summary, highlighting benefits of final design.
| Confirmation that a holistic wellbeing strategy is in place and is reflected within the option assessment / site selection (provide examples). |  | Confirmation that a holistic wellbeing strategy is in place and is reflected within the design (provide examples). |  | Summary of contribution / impact design is expected to have on each of the five wellbeing issues. |  | Confirmation that wellbeing benefits of the building have been communicated to end users during handover and occupation stage.
W2: Indoor environmental quality | Confirm proposed Internal Environmental Quality (IEG) Strategy, covering. |  | Confirm proposed Internal Environmental Quality (IEG) Strategy, covering. |  | Confirmation of detailed modelling to reflect end use and IEQ in use predictions. |  | Confirmation that detailed simulation reports represent the 'as built' building and that these are made available to client.
| Confirmation capacity & expansion modelling for key functions indoors and outdoors, e.g. patient views & access to nature, undertaken and influenced option / site selection. |  | Detailed thermal comfort analysis demonstrates no significant overheating risk. Confirm CIBSE TM52 and / or CIBSE TM 59 compliance. |  | Detailed thermal comfort analysis demonstrates no significant overheating risk. Confirm CIBSE TM52 and / or CIBSE TM 59 compliance. |  | Detailed thermal comfort analysis demonstrates no significant overheating risk. Confirm CIBSE TM52 and / or CIBSE TM 59 compliance.
| Confirmation modelling / assessment of natural ventilation & daylight quality and views from key occupied spaces, influenced option / site selection e.g. climate based daylight, CIBSE TM52. |  | Results of climate based daylight modelling confirm quality and provision of daylight and visual comfort levels for all occupied spaces. |  | Results of climate based daylight modelling confirm quality and provision of daylight and visual comfort levels for all occupied spaces. |  | Results of climate based daylight modelling confirm quality and provision of daylight and visual comfort levels for all occupied spaces:
| Confirmation acoustic assessment influenced option / site selection e.g. SHTM 08-01 or pre-agreed alternative. |  | Confirmation acoustician has advised on noise issues and design is in accordance with recommendations. Confirm SHTM08-01 or alternative pre-approved acoustic standard. |  | Confirmation acoustician has advised on noise issues and design is in accordance with recommendations. Confirm SHTM08-01 or alternative pre-approved acoustic standard. |  | Confirmation acoustician has advised on noise issues and design is in accordance with recommendations. Confirm SHTM08-01 or alternative pre-approved acoustic standard
| Confirmation appropriate pollutants, air, water & land quality assessments influenced option / site selection e.g. Estates, Authorising Persons, SEPA. |  | Confirmation indoor air quality strategy is designed to achieve CO2 levels of <900ppm for relevant occupied spaces. |  | Confirmation indoor air quality strategy is designed to achieve CO2 levels of <900ppm for relevant occupied spaces. |  | Confirmation indoor air quality strategy is designed to achieve CO2 levels of <900ppm for relevant occupied spaces.
| Confirmation HAI SCRIBE influenced option assessment / site selection. |  | Confirmation of TVOCs (<0.3mg/m3) and Formaldehyde (<0.1mg/m3) levels - to be achieved through the specification of natural / low emission materials. |  | Confirmation of TVOCs (<0.3mg/m3) and Formaldehyde (<0.1mg/m3) levels - to be achieved through the specification of natural / low emission materials. |  | Confirmation of TVOCs (<0.3mg/m3) and Formaldehyde (<0.1mg/m3) levels - to be achieved through the specification of natural / low emission materials.
| Confirmation current and future community impact and equalities assessment influenced option assessment / site selection. |  | Confirmation that the design has considered impact of movement of air, dispersion of odour and air pollutants and proposes suitable indoor air quality strategy. |  | Confirmation that the design has considered impact of movement of air, dispersion of odour and air pollutants and proposes suitable indoor air quality strategy. |  | Confirmation that the design has considered impact of movement of air, dispersion of odour and air pollutants and proposes suitable indoor air quality strategy:
Circularity | Update evaluation matrix to coincide with the completion of the (IA) Early OBC stage. |  | Update evaluation matrix to coincide with the completion of the Final OBC stage. |  | Update evaluation matrix and report any changes at Final FBC stage. |  | Update evaluation matrix and report any changes at pre handover stage.
CE: Circular design and construction practices | Confirmation circularity assessment influenced option appraisal / site selection. |  | Confirmation of proposed strategies and actions for designing out waste. |  | Confirmation of resource management approach and metrics for construction stage. |  | Confirmation of volume of waste generated (tonnes / m3) and diversion of non-hazardous waste from landfill (%).
| Confirmation that use & lifetimes of key current and proposed resource elements are assessed & optimised, both in preferred option / site selection. |  | Confirmation of targeted resource efficiency / waste reduction benchmarks, levels of recycled materials, recyclable material and responsibly sourced products. |  | Confirm project team have undertaken a level of viability testing via supply chain engagement routes. |  | Summary of benefits as a result of applying circular design and construction principles, including any cost benefits and levels of recycled and recyclable materials (%age).
Climate Change | Update evaluation matrix to coincide with the completion of the (IA) Early OBC stage. |  | Update evaluation matrix to coincide with the completion of the Final OBC stage. |  | Update evaluation matrix and report any changes at Final FBC stage' |  | Update evaluation matrix and report any changes at pre handover stage
CC1: Operational emissions | Confirmation that Net Zero aspiration (or negative operational GHG tCO2e) assessed and influenced option appraisal / site selection. |  | Net Zero aspiration (targeting net zero or negative operational GHG emissions, reported as tCO2e). |  | Net Zero status. |  | Net Zero status.
| Confirmation that EUI prediction (kWh/m2/yr) assessed and influenced option appraisal / site selection. |  | EUI prediction (kWh/m2/yr). |  | EUI prediction. |  | EUI prediction: Client in receipt of copy of the 'as built' BRUKL / Section 6 / EPC. Client in receipt of operational energy model / ‘digital twin’.
CC2: Embodied carbon | Confirm embodied carbon (kgCO2e/ m2) assessed and influenced option assessment / site selection. |  | Confirm embodied carbon baseline (kgCO2e/m2). |  | Confirm embodied carbon target (kgCO2e/m2). |  | Confirm embodied carbon (kgCO2e/m2).
| Confirm whole life carbon assessed and influenced option / site selection. |  | Confirm Whole Life Carbon objectives. |  | Confirm Whole Life Carbon objectives. |  | Confirm Whole Life Carbon objectives have been met.
CC3: Water consumption | Confirm water safety assessed and influenced option / site selection. |  | Confirm metering strategy, specification and location of water sub-meters. |  | Confirmation of pulsed output sub-meters and / or level of compatibility with BMS. |  | Confirmation all sub-metring as been fully commissioned and programmed to work with BMS.
| Confirm water consumption & efficiency assessed and influenced option / site selection. |  | Confirm specification of water leak detection system for site and boundary. |  | Confirmation of leak detection system and level of compatibility with BMS. |  | Confirmation a leak detection system is fully programmed (confirmation of pre-set values) and commissioned to work with BMS.
| Confirm communinty water impact e.g. flood, SUDS, pollution; assessed and influenced option / site selection. |  | Confirm specification of water efficiency strategy. |  | Confirmation of reduced levels of water consumption. |  | Confirmation installed features, appliances, fixtures and fittings support a reduction in water consumption levels.
CC4: Environmental security | Confirm Green Space Factor assessed and influenced option / site selection. |  | Confirm design is targeting Green Space Factor of at least 0.4. |  | Confirmation of targeted Green Space Factor and delivery of valued greenspace. |  | Confirmation of Green Space Factor.
| Confirm net biodiversity assessed and influenced option / site selection. |  | Confirm design is proposing to support a net biodiversity gain. |  | Details of proposed biodiversity maintenance strategy. |  | Confirmation of net biodiversity gain (details and value).
| Confirm site flood risk level and proposed water management assessed and influenced option / site selection. |  | Confirmation of site flood risk level and proposed water management. |  | Confirmation of responsible surface water management strategy. |  | Confirmation of peak rate surface water improvement run-off and run-off volume and climate change allowance.
| Confirm pollution, e.g. air, water, land, light, noise; assessed and influenced option / site selection. |  | Confirm specification of pollution control / mitigation strategy (water, air, noise etc.). |  | Confirmation of expected site wide management and maintenance requirements. |  | Confirm development has been designed to have zero negative impact to local pollution levels (water, air, noise etc.).
| Confirm equality & community impact e.g. place-making, heritage, mass, orientation, inclusive design; assessed and influenced option / site selection. |  | Confirm site optimisation strategy (layout, orientation, inclusive design). |  | Confirmation that site optimisation strategy has been designed to support performance outcomes. |  | Confirm range of benefits that the site optimisation strategy is intended to support.
CC5: Active and sustainable transport | Confirm active travel and sustainable transport potential assessed and influenced option / site selection. |  | Confirm active travel and sustainable transport strategy proposed for development and targeted behavioural shift. |  | Confirmation that the proposed design embraces the Places for Everyone principles. |  | Client in receipt of site-specific Travel Plan.
Archived August 2025

## Notes and Actions
Notes and Actions
Reference |  | Notes | Actions | By Date | Owner /Lead responsible | Key Stakeholders Engaged | Completed
W1 Healthy Places - Total Wellbeing
W1.1 | Strategic priorities
W1.2 | Total wellbeing
W1.3 | Holistic approach to wellbeing
W1.4 | Integrated approach
W1.5 | Approve final specifications
W1.6 | On-going engagement
W1.7 | Aftercare
W1.8 | Structured POE programme
W2 Wellbeing IEQ
W2.1 | Strategic priorities
W2.2 | Indoor Environmental Quality
W2.3 | Comfort analysis
W2.4 | Monitoring indoor environments
W2.5 | Modelling and change control
W2.6 | Acoustics testing & inspection
W2.7 | Aftercare
W2.8 | Structured POE programme
CE Circularity
CE1.1 | Strategic priorities
CE1.2 | Zero waste solutions
CE1.3 | Option / Site assessment & strategy
CE1.4 | Supply chain
CE1.5 | Technical update & contracts
CE1.6 | Responsible construction practices
CE1.7 | Lessons & measuring success
CE1.8 | Structured POE
CC1 Operational GHG
CC1.1 | Strategic priorities
CC1.2 | Net zero
CC1.3 | Passive design analysis
CC1.4 | Performance review workshop
CC1.5 | Quality & Change control
CC1.6 | Quality monitoring
CC1.7 | Commissioning, training & aftercare
CC1.8 | Structured POE
CC2 Embodied Carbon
CC2.1 | Strategic priorities
CC2.2 | Life Cycle Assessment
CC2.3 | Embodied carbon
CC2.4 | Reporting and updates
CC2.5 | Communication and engagement
CC2.6 | Monitoring and reporting
CC2.7 | Final reporting
CC2.8 | Structured POE
CC3 Water Consumption
CC3.1 | Strategic priorities
CC3.2 | Water hierarchy
CC3.3 | Water efficiency
CC3.4 | Sub-metering strategy
CC3.5 | Leak detection
CC3.6 | Quality & Change control
CC3.7 | Communication
CC3.8 | Structured POE
CC4 Environmental Security
CC4.1 | Strategic priorities
CC4.2 | Environmental security & GSF
CC4.3 | Option / Site appraisals
CC4.4 | Integrated design approach
CC4.5 | Planning for aftercare
CC4.6 | Quality & Change control
CC4.7 | Aftercare
CC4.8 | Structured POE
CC5 Active Travel & Sustainable Transport
CC5.1 | Strategic priorities
CC5.2 | Active travel & sustainable transport
CC5.3 | Option / Site appraisals
CC5.4 | Safety and security
CC5.5 | Route planning and signage
CC5.6 | Travel Plan
CC5.7 | Aftercare
CC5.8 | Structured POE
Archived August 2025

## Evaluation Matrix
Evaluation Matrix
Evaluation Matrix |  | Wellbeing | [5 empty] | Circularity |  |  | Climate Change
SCIM | RIBA Plan of Work | Ref. | W1. Healthy Places - Total Wellbeing |  | Ref. | W2. Indoor Environmental Quality |  | Ref. | CE1. Circular Design and Construction |  | Ref. | CC1. Operational Emissions |  | Ref. | CC2. Embodied Carbon |  | Ref. | CC3. Water Consumption |  | Ref. | CC4. Environmental Security |  | Ref. | CC5. Active Travel and Sustainable Transport
Strategic Assessment | 0 Strategic Definition | W1.1 | Consider how a design that delivers healthy places and supports total wellbeing through the creation of quality, accessible and desirable spaces will support NHSScotland's value and sustainability strategic investment priorities. | 0 - Not Started | W2.1 | Consider how indoor environmental quality will support NHSScotland’s value and sustainability strategic investment priorities (Person Centred, Safe, Effective Quality of Care, Health of Population and Value & Sustainability). | 0 - Not Started | CE1.1 | Consider how circular economy principles will support NHSScotland’s value and sustainability strategic investment priorities. | 0 - Not Started | CC1.1 | Consider how a building designed to achieve net zero operational GHG emissions will support NHSScotland’s value and sustainability strategic investment priorities. | 0 - Not Started | CC2.1 | Consider how a building that achieves significantly reduced levels of embodied carbon will support NHSScotland’s value and sustainability strategic investment priorities. | 0 - Not Started | CC3.1 | Consider how a building that integrates a water efficiency strategy can support an overall reduction in the operational carbon footprint and will support NHSScotland’s value and sustainability strategic investment priorities. | 0 - Not Started | CC4.1 | Consider how a development that delivers environmental security and valuable greenspace will support NHSScotland’s value and sustainability strategic investment priorities. | 0 - Not Started | CC5.1 | Consider how a development that integrates and prioritises active travel and more sustainable transport in a safe and inclusive way will support NHSScotland’s value and sustainability strategic investment priorities. | 0 - Not Started
Initial Agreement Initial Design Statement | 1 Preparation and Briefing | W1.2 | Within the brief, commit to: - Promoting design that prioritises physical, social, mental, occupational and economic wellbeing of all users; - Delivering quality space through the adoption of the Place Standard, AEDET and NDAP. | 0 - Not Started | W2.2 | Within the brief, commit to: - Prioritising physical wellbeing of users by ensuring internal environments are designed to create healthy and comfortable spaces for all; - Detailed IEQ strategy with defined perf. parameters. | 0 - Not Started | CE1.2 | Within the brief, commit to circular design and construction processes & circular procurement hierarchy - prevent / reduce / reuse / recycle / recover Identify opportunities for intervention - refer to industry guides e.g. UKGBC circular economy guide for construction clients. | 0 - Not Started | CC1.2 | Within the brief, commit to: Delivery of a net zero GHG emissions development; Use of existing data to inform an EUI benchmark; & Min. design performance measures (as referenced within guidance document). | 0 - Not Started | CC2.2 | Within the brief, commit to: A lower embodied carbon development; Comprehensive embodied carbon reduction strategy;& Adoption of consistent methodology for WLC analysis. | 0 - Not Started | CC3.2 | Within the brief commit to: -Adopting the water efficiency hierarchy for the development; . - Water efficient components; - Monitoring and leak detection; - Responsible procurement: EU water label scheme | 0 - Not Started | CC4.2 | Within the brief commit to: - A purposeful landscape led approach - option / site appraisal and establish a baseline; - Environmental impact and mitigation strategies; - A Green space factor of at least 0.4. | 0 - Not Started | CC5.2 | Within the brief commit to: Removing the need to travel - Digi health & shared / complementary services; Prioritising and incentivising active travel and sustainable transport; Safe movement of people & goods; Deliver a resilient transport infrastructure. | 0 - Not Started
Early OBC Final Design Statement | 2 Concept Design | W1.3 | Design driven by user needs; clinical and functional - a clear connection between design and users; Holistic approach to wellbeing - identify performance parameters that support identified wellbeing outcomes; Creation of valuable internal and external spaces. | 0 - Not Started | W2.3 | Stakeholder engagement - Recognise and acknowledge feedback from key user groups; Detailed dynamic simulation model - early design analysis, ensuring accuracy of data; IEQ - strategy and technical performance review. | 0 - Not Started | CE1.3 | Inform project strategy with suitable metrics: - Design out waste and pollution / Responsible design, procurement and construction practices / Design for assembly, disassembly and recoverability. - Identify intervention points & analyse design. | 0 - Not Started | CC1.3 | Initial and detailed passive design analysis; Consider healthcare operational process and the accuracy and availability of operational templates; Early detailed simulation modelling and results review workshop; Review optimisation and renewables strategy. | 0 - Not Started | CC2.3 | Options appraisal- refurb. or new build / site selection. Establish baseline reporting figure to guide design; Detailed carbon reduction strategy; Ensure accuracy and robustness of data; Iterative WLC assessment - options appraisals; Prioritise EPD and responsible product sourcing. | 0 - Not Started | CC3.3 | Options appraisal for reducing consumption for building and landscaping: - Feasibility study for rainwater harvesting system; - Avoid the need for dedicated irrigation that requires mains supply. - Effective strategy for waste water pollution | 0 - Not Started | CC4.3 | Early site appraisals: landscape and environmental. Environmental security demonstrated through site optimisation & options appraisals; Promote design that can enable the active and inclusive use of the estate in clinical interventions. | 0 - Not Started | CC5.3 | Site appraisals: Infrastructure / current trends / accessibility / local environment / capacity etc. Intuitive concept designs: safe movement / wayfinding / prioritisation / integration / green infrastructure etc. Engagement: Feedback captured & acknowledged. | 0 - Not Started
Review (pre-option/site selection/masterplan) |  | Internal approval
OBC | 3 Spatial Coordination | W1.4 | Integrated approach: High-quality, ergonomic design and creation of spaces that support all aspects of wellbeing; Space that encourages movement; Encouraging social relationships; Purposeful design; Inclusive and accessible design. | 0 - Not Started | W2.4 | Monitoring and control strategy: - Intuitive systems to support user interaction; - Responsive control strategy; - Remote monitoring and programming, review with Estates Management and client representatives. | 0 - Not Started | CE1.4 | Supply chain engagement and viability testing: Review of circular product innovations; Review existing and new procurement routes (services as opposed to products). On-going reviews: Monitor design developments, conduct regular reviews, evaluate the overall impact . | 0 - Not Started | CC1.4 | Performance review workshop: - Detailed Simulation Model walkthrough: Consider operational assumptions, internal environmental conditions, performance outcomes & EUI; - Detailed review of metering, programme & control; - CTH and Estates / FM strategy review. | 0 - Not Started | CC2.4 | Carbon budgets, reporting and updates - Iterative process. Life Cycle Assessment and Life Cycle Cost integration to inform options appraisal. Continue to review and update during design development stages. | 0 - Not Started | CC3.4 | Detailed review of water sub-metering provision, location, specification and operation. Full integration with BMS platform for ease of monitoring and reporting. | 0 - Not Started | CC4.4 | Integrated design development approach: - Purposeful landscaping, valuable greenspace, increase in biodiversity, pollution prevention strategies. End user engagement: - User ownership, connecting communities. | 0 - Not Started | CC5.4 | Safety and security assessment: layout & access, wayfinding, lighting provision, segregation of service vehicle routes, natural segregation & protection. Provision of complementary services: enable active travel and support behaviour shifts. | 0 - Not Started
Review (pre-planning) |  | Internal approval
FBC | 4 Technical Design | W1.5 | Final specifications: - Desirable and usable space: End users feedback and usability testing influences final specification details; Review management and maintenance requirements. | 0 - Not Started | W2.5 | Detailed dynamic simulation modelling - technical design update; IEQ performance parameters - review and update prior to construction work commencing; Management and maintenance - strategy review and draft BUG content. | 0 - Not Started | CE1.5 | Update results of LCA, LCC and carbon budget: Communicate information with full project team and supply chains before moving to construction stage. Encourage circular supply chains: Inform procurement and tender documentation. | 0 - Not Started | CC1.5 | Change control - Approve any changes before construction and agree change control strategy; Quality assurance - Plan for inspection during construction stage (who, how and when?) Soft Landings review - Technical design 'reality checking'. | 0 - Not Started | CC2.5 | Supply chain engagement - viability assessment; Inform tender / procurement documentation. Update carbon budgets at technical design stage and obtain LCA verification (final technical design). | 0 - Not Started | CC3.5 | Specification of leak detection system: - Automated alert, programmable system; - Integration with BMS (for remote monitoring, programming and alerts). | 0 - Not Started | CC4.5 | Plan for aftercare: -Site wide management and maintenance strategies; - Training and handover strategies agreed - via soft landings approach. | 0 - Not Started | CC5.5 | Effective, friendly route planning & signage: - Clear zoning strategy; - Person-centred environment - Safe & effective; - Consistent and inclusive; - Friendly, positive communication; - Assist in an entire journey (site and building). | 0 - Not Started
Review (pre-construction) |  | Internal approval
Construction & Commissioning | 5 Manufacturing and Construction | W1.6 | Provision and purpose of design features and accessible and inclusive spaces to be included and communicated within building user guides. | 0 - Not Started | W2.6 | Quality assurance and pre-completion testing to be completed prior to handover / occupation: - Acoustic pre-completion inspection and testing; - Internal environment - air quality results etc. | 0 - Not Started | CE1.6 | Responsible construction practices: - Responsible procurement and resource management strategies; Agreed metrics and reporting schedule. Change control: - Management of issues, client approval required. | 0 - Not Started | CC1.6 | Quality monitoring: -Quality assurance inspections & client reporting; -Programme of physical testing: fabric integrity / air-quality. Building user guides - review and sign-off | 0 - Not Started | CC2.6 | Carbon management and mitigation strategy implemented and impacts monitored and reported during construction; Quality assurance - Scheduled reviews and regular monthly reporting. | 0 - Not Started | CC3.6 | Quality assurance: - Change control procedure in place requiring client sign-off. | 0 - Not Started | CC4.6 | Quality and change control: - Site champion nominated to monitor, manage and report on all environmental security and enhancement aspects. | 0 - Not Started | CC5.6 | Site specific travel plan: - Travel and transport strategy communicated to all users (staff, patients, visitors) in accessible formats; - Travel plan to form part of a wider building user guide for staff. | 0 - Not Started
Project Monitoring & Evaluation | 6 Handover | W1.7 | Aftercare strategy - part of soft landings approach: - Showcasing of total wellbeing features communicated to end users during handover and aftercare sessions. | 0 - Not Started | W2.7 | Aftercare strategy - part of soft landings approach: - Communication and promotion of internal environment quality aspects and associated benefits to end users during handover and aftercare sessions. - Seasonal commissioning inspections. | 0 - Not Started | CE1.7 | Lessons learned and measuring success: - Workshop to review benefits of applying circular economies to project; - Lessons and learning captured in report. | 0 - Not Started | CC1.7 | CTH strategy in action - review aftercare programme; EPC - Net Zero Carbon 'as-built'; Client in receipt of multi-disciplinary model - BIM, Detailed Simulation Modelling, (to support asset management, maintenance, in-use, adaptation). | 0 - Not Started | CC2.7 | As-built' review and final WLC assessment report; Carbon budget comparator exercise; Review and document lessons learned. | 0 - Not Started | CC3.7 | Programming of leak detection systems - client / end user engagement as part of soft landings training and aftercare programme. | 0 - Not Started | CC4.7 | Aftercare: - Training and aftercare as part of soft landings, covering management and maintenance strategies. | 0 - Not Started | CC5.7 | Handover and aftercare - feed into soft landings activities: - Communication and promotion of travel and transport strategy to end users during handover and aftercare sessions. | 0 - Not Started
Review (pre-occupation) |  | Internal approval
Project Monitoring & Evaluation | 7 Use | W1.8 | Extended POE monitoring - Functional performance analysis: occupant consultation, use of space, qualitative data, positive user interactions. Data disclosure - Capture and share lessons. | 0 - Not Started | W2.8 | Extended POE - Functional performance analysis - qualitative and quantitative data; occupant consultation, internal environment monitoring; link with KSAR process. Data disclosure - Capture and share lessons. | 0 - Not Started | CE1.8 | Extended POE - Review of circular business models in operation, updated LCC and WLC operational models Data disclosure- knowledge share, support supply chain development | 0 - Not Started | CC1.8 | FM contracts - performance based: energy consumption and prioritising comfort & wellbeing; Extended POE - commence 3 year programme; Data disclosure - capture and share lessons. | 0 - Not Started | CC2.8 | Extended POE - WLC impacts monitored and reported during operation and at end of life; Data Disclosure - capture and share lessons. | 0 - Not Started | CC3.8 | Extended POE - consumption monitoring, maintenance and management; Data Disclosure - capture and share lessons. | 0 - Not Started | CC4.8 | Extended POE - effectiveness of pollution control & landscape features; use and perceived value of outdoor space; Data Disclosure - capture and share lessons. | 0 - Not Started | CC5.8 | Extended POE - Strategy impact and efficiency review: monitoring of trends, staff, patient and visitor impact; Data Disclosure - capture and share lessons / findings. | 0 - Not Started
Review (in-use) |  | Internal approval
Key:
0 - Not Started
1 - Commenced
2 - Established
3 - Almost complete
4 - Complete
N/A
Archived August 2025

## Completion Summary
Completion Summary
| Completion Status | Theme | Progress (%) | 0: Not Started | 1: Commenced | 2: Established | 3: Almost Complete | 4: Complete | Not Applicable | Applicable Total
| Wellbeing | W1. Healthy Places - Total Wellbeing | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | W2. Indoor Environmental Quality | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Circularity | CE1. Circular Design and Construction | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
| Climate Change | CC1. Operational Emissions | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CC2. Embodied Carbon | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CC3. Water Consumption | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CC4. Environmental Security | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | CC5. Active Travel and Sustainable Transport | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 0
Archived August 2025

## Graphs and Scoring (hidden)
Performance Summary
Climate Change | % achieved | Yes | No | N/A | Applicable Total | Circularity | % achieved | Yes | No | N/A | Applicable Total | Wellbeing | % achieved | Yes | No | N/A | Applicable Total
CC1. Operational Emissions | #DIV/0! | 0 | 0 | 0 | 0 | CE1. Circular Design and Construction | #DIV/0! | 0 | 0 | 0 | 0 | W1. Healthy Places - Total Wellbeing | #DIV/0! | 0 | 0 | 0 | 0
CC2. Embodied Carbon | #DIV/0! | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | W2. Indoor Environmental Quality | #DIV/0! | 0 | 0 | 0 | 0
CC3. Water Consumption | #DIV/0! | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
CC4. Environmental Security | #DIV/0! | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
CC5. Active Travel and Sustainable Transport | #DIV/0! | 0 | 0 | 0 | 0 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Total | #DIV/0! | 0 | 0 | 0 | 0 | Total | #REF! | #REF! | #REF! | #REF! | #REF! | Total | #REF! | #REF! | #REF! | #REF! | #REF!

## Post Occupancy Evaluation
Post Occupancy Evaluation
|  | FBC | POE
Post Occupancy Evaluation Monitoring | Suggested Measure | Design Prediction | Handover Capture | Year 1 Data Capture | Year 2 Data Capture | Improvement On Year 1 | Year 3 Data Capture | Improvement On Year 2
Wellbeing
Occupant comfort levels:
Internal air quality in each monitored space | <900 CO2 ppm
Internal temperature in each monitored space | Compliance with CIBSE TM 52 and / CIBSE TM 59.
Noise | Compliance with SHTM 03-01. No breach of acoustic levels / no formal complaints raised.
Quality spaces that are fit for purpose (e.g. confirmation of desirable space and that different functional areas are operational and effectively meet end user needs) | User feedback e.g. occupant survey and focussed discussion workshops.
Adaptability of space | Building / areas support a change in use / expansion.
Flexibility of space | Building / areas accommodates a variety of uses as per end user needs.
Accessible internal and external spaces | Feedback from accessible and inclusive end user testing.
Valued greenspace | Availability, accessibility and reported use of greenspace.
Active travel | Travel survey data.
Occupant satisfaction | Staff comfort levels, occupant satisfaction rates, perceived levels of wellbeing (survey feedback, focussed workshop discussion sessions, results from wellbeing scale).
Circularity
Resource efficiency | Volume of waste generated.
Reporting of waste streams (volume reused / recycled recovered / disposed).
Management and maintenance | LCC predictions compared with in use data (e.g. expected levels of performance / longevity).
Circular procurement | Waste streams and Carbon budgets.
Climate Change
Operational GHG emissions | tCO2e per annum.
Energy Use Intensity | kWh/m2/yr
Renewable technology contribution | kWh/m2/yr
Performance and security of energy supply | Quality inspection result / incidence of failure
Water management | Water management effectiveness (incuding waste water and detection of any water leaks, including volumes).
Water consumption (volume per annum - breakdown per metering strategy).
Landscape management | Maintenance of greenspace (effectiveness of strategy and annual cost).
Maintenance of biodiversity on site (effectiveness of strategy and cost).
Pollution control strategies | Recorded incidences requiring pollution control measures (flooding, water, air, noise etc.).
Archived August 2025

## Stakeholder List
Stakeholder List
SURNAME | Name | Role | Organisation | E-mail | IA/eOBC | OBC | FBC | POE
COUNT | 0 |  |  |  | 0 | 0 | 0 | 0
Archived August 2025

## Sheet1 (hidden)
Board Name | Yes
NHS Ayrshire and Arran | No
NHS Borders | N/A
NHS Dumfries and Galloway
NHS Western Isles
NHS Fife
NHS Forth Valley
NHS Grampian
NHS Greater Glasgow and Clyde
NHS Highland
NHS Lanarkshire
NHS Lothian
NHS Orkney
NHS Shetland
NHS Tayside
Public Health Scotland
Healthcare Improvement Scotland
NHS Education for Scotland
NHS National Waiting Times Centre
NHS24
Scottish Ambulance Service
The State Hospitals Board for Scotland
NHS National Services Scotland
Other

## Guidance (hidden)
Climate Change
Issue | Operational emissions
Outcome | Net zero Greenhouse Gas emissions
Performance verification | 'As built' building information confirms that the amount of Greenhouse Gas emissions associated with the building's operational energy on an annual basis is zero or negative.
SCIM | RIBA Plan of Work | Guidance
Strategic Assessment | 0 Strategic Definition | Apply POE learning & adopt soft landings approach | A net zero Greenhouse Gas emissions (GHG) building has zero (or negative) emissions associated with the building’s annual operational energy. It is a highly energy efficient building, powered 100% by on-site and / or off-site renewable energy and achieves a level of energy performance in-use in line with national climate change targets. Net zero Set a clear and uncompromising project outcome, to be included in the project brief, in relation to operational emissions; a requirement to design and construct a net zero GHG emissions building. | Commitment to design and construct a net zero GHG emissions development. referenced within SCIM and project brief
Initial Agreement Initial Design Statement | 1 Preparation and Briefing |  | The Energy Use Intensity (EUI) is a measure of the total energy consumed in a building annually; a metric that is solely dependent on how well the building will perform in-use, measured in kWh/m2.yr. An EUI includes all regulated and unregulated energy consumption. EUI Inform an EUI benchmark that can be specified in the brief and utilised during early design stages. Utilise existing data on the NHSS energy monitoring and targeting site, identifying best practice projects where possible, to inform the EUI. The building’s energy demand for space heating and cooling can be significantly reduced through enhanced fabric performance and passive design measures. Performance measures should be specified within the brief to encourage design development that promotes a fabric first approach. Space heating Reduce space heating demand. Adopt a passive design target of <15 kWh/m2.yr or utilise existing data on the NHSS energy monitoring and targeting site, identifying best practice projects where possible, to inform the benchmark. Fabric performance Require the specification of highly efficient fabric and external shading design to reduce the heating and cooling demand. Promote passive design and fabric efficiency by requiring the following indicative fabric performance measures: Walls <0.15 W/m2K Windows <1.0 W/m2K Floor <0.12 W/m2K Doors <1.2 W/m2K G-value of glass <1.2 W/m2K Roof <0.12 W/m2K Air permeability <1 m3/h.m2@50Pa Thermal bridges can account for considerable heat loss in a building and as buildings become better insulated this becomes even more significant. Thermal bridges can create localised cold-spots, leading to condensation build-up or mould growth. Losses are calculated by considering junction PSI-values and a building’s y-value. The lower the U-values, Y-values and PSI-values, the lower the fabric heat loss. Thermal bridge losses Limit the overall heat loss arising from thermal bridge losses by setting a maximum y-value of 0.04 W/m2K. Request that junction PSI-values, for each of the junctions where the building elements meet, are quantified and improved where possible. Prior to optimising building systems’ to satisfy predicted consumption levels, energy demand should first be limited, as far as reasonably possible, through the building fabric and passive measures. To further increase the overall efficiency of the building in-use, the specification of energy efficient building systems and the integration of smart energy management systems are required. Improvements should include highly energy efficient HVAC, lighting and vertical transport systems as well as the integration of intuitive and responsive building management systems. Designs should take account of recommended heating and hot water coefficients of performance (COP) and Seasonal Performance Factors. The physical wellbeing of building occupants should be considered alongside energy reductions. These include considerations around indoor air quality, daylight and overheating. Further guidance is included within the Wellbeing section of this document. System efficiency measures Reference trusted sources when considering setting limits for lighting power density, e.g. EU Green Public Procurement Indoor Lighting Technical Background Report where normalised lighting power density for hospital wards and examination rooms is recommended as 3.5 – 4 W/m2/100lux. Require the specification of heat pumps with a Seasonal Coefficient of Performance of 2.8 or above, where the COP for GSHPs is over 4 and ASHPs is over 3. Where Mechanical Ventilation is deemed the most suitable system, Mechanical Ventilation with Heat Recovery (MVHR) with an efficiency of at least 90% is required. Energy efficient solutions are required to be specified for any vertical transport systems, with the number and size dictated by demand and usage patterns. The use of regenerative drives should be considered and energy efficient features should be specified for lighting, standby options and VVF control of the drive motor. BEMS, metering, control and programming …….. | Utilise existing data to inform EUI benchmark; requirement to report this Min. design performance measures specified. details of actual performance values within guide
Early OBC Final Design Statement | 2 Concept Design |  | Factors such as building massing, layout, orientation, fabric design, daylighting provision, ventilation strategies and thermal mass can significantly affect the heat gains and losses in a building. An early passive design analysis can help to inform a design solution that minimises reliance on active building services systems. Passive design analysis Require a detailed passive design analysis to be delivered and for the results to inform the conceptual designs. The initial findings should be presented to the client during early concept design stages. As a minimum, the passive design analysis should cover: Site location / Site weather / Microclimate / Building layout / Building orientation / Building form / Building fabric / Self-shading and external shading features / Thermal mass or other fabric thermal storage / Building occupancy type / Daylighting strategy / Window to wall ratio / Ventilation strategy / Adaptation to climate change. Requirement for renewable energy feasibility study - low carbon - demand response ….detail considerations and favourable options The accuracy of output from a dynamic simulation model is highly influenced by the level of accuracy and detail that is fed into the model. In order to help adequately address any perceived performance gap issues, it is vitally important that the information collated and used to predict theoretical performance during design development stage accurately represents the actual operational patterns, as far as reasonably possible. This will be a collaborative process. It is advised that the client develop standard operational templates and, over time, builds a library that can be used as a source of information. Operational templates Assumptions in relation to occupancy rates and usage patterns must be realistic and accurately reflect how the operational building will function. Detailed information on the use of the building should be collated during detailed stakeholder engagement exercises. Operational templates are required to be populated with information captured during stakeholder engagement sessions. This will detail how each intended space is required to operate, expected behavioural and occupancy patterns and will identify the required equipment and services to allow this space to be fully functional. This information should be sourced from end user groups and agreed with the client at as early an opportunity as possible. Dynamic simulation modelling (DSM) will play an important part in the transition to net zero. Modelling should evolve throughout the design process and post-handover, into operation and there will be requirements for different types and levels of information at each stage. The accuracy and robustness of dynamic simulation models are heavily influenced by the accuracy of the information that is provided and utilised when predicting in-use building performance scenarios. To deliver credible and valuable results, information that accurately reflects how the building will be operated when in-use must be sourced, verified and utilised. Clients, project teams and wider stakeholder must all take responsibility in providing this information and ensuring its accuracy. The decisions drawn from the results of the modelling also need to be shared across all project stakeholders. Dynamic Simulation Modelling Modellers are expected to hold the required level of training and demonstrate competency in order to deliver and adequately analyse results and provide credible recommendations at each stage of project development. There is a requirement to review the input data and outcomes with the client at every project stage. Evidence of Quality Management is a requirement and is expected to include review and verification of input data and output results by suitably qualified and experienced independent 3rd party experts at each stage in the project where modelling has been carried out. There is a need for collective responsibility and collaboration when collating comprehensive data relating to the forecasting of the building performance in-use. All assumptions must be reviewed and agreed with the client. Operational templates (for each room and space) must be prepared and agreed with wider stakeholder and end user groups to ensure accuracy of input data. Early, in-depth stakeholder consultation with appropriate user groups is expected to ensure provision and accuracy of this data. The client must have the opportunity to spend adequate time with the modeller to conduct an in-depth review of input data, ensuring accuracy and robustness, at an early stage in the project and throughout. The NHSS modelling guide must be followed. EUI reporting required during appraisal of concept design. | Availability of operational templates; Detailed passive design analysis; Detailed dynamic simulation modelling; Demand response and renewables strategy. detailed approach within guide
Final OBC Early FBC | 3 Spatial Coordination |  | To evaluate and ensure robustness of operational performance predictions, request disclosure of key building performance metrics prior to planning approval. If targets are not being met, this allows for an opportunity to obtain further clarification and make changes where required. The Project team are required to arrange a detailed performance review workshop with client prior to planning submission. The client side estate management team should be represented at this workshop. The workshop will include a detailed DSM walkthrough, ensuring accuracy and robustness: - Review of minimum design performance measures, predicted operational performance and EUI - Review of operational assumptions (based on information from operational templates and client / Estates input) - Internal environmental conditions (ensuring comfort and wellbeing of occupants) - Review of metering, management, zoning, programme and control strategy (opportunity for optimising operational efficiency) - Appropriate sizing / specification of building systems to limit over-engineering (demonstrate passive design measures and fabric enhancement have significantly reduced demand) | Client DSM walkthrough and sign-off: -Min. design perf. measures and EUI -Operational assumptions -Internal environmental conditions -Metering, programme and control
Performance review - pre-planning |  |  | Internal approval - Complete evaluation matrix and report on net zero aspirations and EUI predictions.
Final FBC | 4 Technical Design |  | Prior to work commencing on site, undertake a performance verification exercise of the final design. Request a compliance summary report from the project team and ensure all agreed performance targets are being met. Effectively communicate the project ambitions with the contractor and plan for quality assurance throughout every stage of the construction and handover stages. Establish a change control procedure that requires full communiction and client sign-off. Request that full consideration is given to the level of impact that any proposed change may have on the building's operational performance and that this is highlighted and discussed with the client prior to any changes being made or agreed. Request that a quality assurance plan is developed to monitor and promote good standards and practices during the construction stage. An on-site inspection programme is expected to commicate who will lead on this (e.g. lead designer), how oftern quality inspections will take place and what level of detail will be required. Ensure design aspirations, project outcomes, change control procedures, risk and quality assurance measures are all clealry communicated with contractor before any work starts on site. | Approve any changes before construction; Plan for inspection - build and commissioning - who, how and when?
Performance review - pre-construction |  |  | Internal approval - Update evaluation matrix and report any changes.
Construction & Commissioning | 5 Manufacture & Construction |  | Manage risk and promote higher levels of quality throughout the construction stage by ensuring regular quality assurance inspections are taking place, all change control procedures require client approval and that a requirement of physical testing is put in place. Ensure all systems and services are collectively commissioned and programmed to operate as intended prior to handover stage and a member of the client estates' team has the opportunity to benefit from a detailed walkthrough of all programming and controls. This will provide an opportunity for the building to operate efficiently from the very start of the in use stage. Request that procedures are put in place to monitor and report on quality assurance on-site and require regular inspections and reporting to take place. Require particular attention to detail in relation to quality of workmanship that could compromise the fabric integrity e.g. enhanced building details, storing, preparation and installation of insulation materials and where services penetrate the building fabric. Ensure a programme of physical testing is completed prior to handover. This should include testing of the fabric integrity and is expected to include air permeability testing and thermography to demonstrate performance with design stages predictions and continuity of insulation. Alocate adeqaute time in the delivery programme for commissining and any re-commissioning of complex and non-complex building services and handover and aftercare workshops to take place in the months prior to completion, following a soft landings approach. Request a cohesive, whole building approach to commissioning to ensure all systems and services are commissioned and programmed to work seamlessly together, and as designed. A system and servies design review should take place between the project team (ideally contractor and lead designer) and an appointed commissioning manager prior to the commissionoing of systems. This should be followed up by a site inspection visit with a representative from the client estates team, prior to handover. Ensure a comprehensive seasonal commissioning programme is agreed and in place prior to handover. This should take place during the first 12 months after occupation and account for differing occupancy patterns and seasonal impacts. | Quality assurance: -Change control procedure - client sign-off -Inspection - client reports -Programme of physical testing - fabric integrity / air-quality
Project Monitoring & Evaluation | 6 Handover |  | A handover procedure and aftercare package that promote a soft landings approach should be prepared, this should follow the approah taken throughout the project and support a smooth transition to the in use phase. It is important to understand how and who will be operating and interacting with the building and making sure that the Building Information is in a useable and digestible format. Identify the levels of information that will benefit each user group and ensure that this is provided prior to handover; a standard Building Manual for detailed information, a quick start guide of key asset information (for estates team / facility managers) and a Building Users Guide for the every day user groups. In order to accurately monitor and compare predicted performance with actual in use performance, a client should request an updated multi-disciplinary model with 'as built' information. This model(s) can support asset management, inform maintenance strategies, monitor in-use performance, consider the viability and impact of future adaptation, plan for end of life etc. Request and plan for the following commissioning and aftercare support: Commissioning manager to schedule a review of the operational systems and services with a representative from the estates team, allowing an opportunity for early fine tuning of systems and services, commencing prior to occupation. End user interactive workshops and guided tours scheduled to take place prior to occupation to smooth transition and aid understanding of the level of interaction and control each user group can expect to exercise. Content must be tailored to support those who use the building and those who manage the building. Contractor to identify an aftercare manager and agree aftercare plan with client. As a minimum this will include commitment to a series of defect review meetings, dates for the seasonal commissioning of building services and a commitment to support post occupancy evaluation. Prior to handover, the following should be provided: EPC - Net Zero Carbon 'as-built' Building User Guides Seasonal Commissioning Programme Level of Aftercare and post occupancy monitoring and Multi-disciplinary model updated with 'as built' information and including: DSM - in use energy, comfort predictions etc. LCC study - maintenance & replacement WLC assessment - 'as built' assessment | EPC - Net Zero Carbon 'as-built'; Client in receipt of multi-disciplinary model (to support asset management, maintenance, in-use, adaptation).
Performance verification - 'as built' / pre-occupation |  |  | Internal approval - Update evaluation matrix and report any changes. Copy of the 'as built' EPC Confirmation of the 'as built' operational performance predictions - net zero and EUI
Project Monitoring & Evaluation | 7 |  | In order to support the efficient operation of the building in use and to collate valuable information that can be used to optimise performance as well as provide knowledge and learning for others, the following should be promoted: FM / asset management contracts to be performance based in relation to energy consumption Structured POE programme to capture data and verify performance outcomes over a minimum reporting period of 3 years (ideally indefinitely) Data disclosure, encouraging full transparency and knowledge share, supporting learning and performance improvement | FM contracts, performance outcomes based on energy consumption; Model based performance analysis; Extended POE; Data disclosure.
Yes
No
N/A
Performance verification - in-use |  |  | Internal approval - Completed POE reporting template
Resources | UKGBC Net Zero Carbon Buildings: A Framework Definition; Climate Change (Emissions Reduction Targets) (Scotland) Act 2019

## Guidance (2) (hidden)
Climate Change
Issue | Embodied carbon
Outcome | Consider net zero in the context of Whole life carbon.
Performance verification | Whole Life Carbon assessment confirms a marked reduction in the level of embodied carbon over the building life cycle (kgCO2e).
SCIM | RIBA Plan of Work | Guidance
Strategic Assessment | 0 Strategic Definition | Apply POE learning & adopt soft landings approach | Embodied carbon refers to the amount of greenhouse gas (GHG) emissions generated to produce a built asset. This includes emissions associated at the following life cycle stages: Product: extraction, manufacture/processing of materials, transportation to site. Construction: assembly of every product and element in the building (energy and water consumption). In-use: maintenance, repair, refurbishment, replacement and emissions associated with refrigerant leakage. End of life: demolition, disassembly waste processing and disposal of any parts of product or building and any associated transportation. Whole Life Carbon (WLC) refers to embodied carbon plus operational carbon. Embodied carbon Commit to a Whole life Carbon approach by setting a requirement in the project brief for a reduction in embodied carbon to be demonstrated over the building life cycle. | Commitment to design and construct a net zero GHG emissions development. referenced within SCIM and project brief
Initial Agreement Initial Design Statement | 1 Preparation and Briefing |  | A WLC assessment is used to inform building design and products that generate the lowest carbon emissions over its whole life. This is measured through a Life Cycle Assessment (LCA), which accounts for the associated emissions at every life cycle stage of a building’s materials and products. Environmental Product Declarations (EPDs) are to be used, where possible, as credible and transparent sources of information that can support LCA studies. The LCA should typically consist of four key steps: 1. Define goal and scope – Promote the design with the least environmental impact. Consistency in approach. 2. Estimate quantities of materials, products and processes – Accuracy of data. Utilising BIM models. 3. Assess environmental impact – Consistent assessment methodology at building level and product level. 4. Interpret the results, refine and re-iterate – Iterative process that will inform design. Creation of carbon budgets. Set a requirement for the project team to deliver an LCA study that follows the methodology outlined in the RICS Professional Statement for Whole life carbon assessment for the built environment. Request that an IMPACT compliant LCA tool is used and that a 60 year study period is referenced. Request the use of products with Environmental Product Declarations over those without. Request that the study is used to inform design with the lowest emissions over its whole life. | Utilise existing data to inform EUI benchmark; requirement to report this Min. design performance measures specified. details of actual performance values within guide
Early OBC Final Design Statement | 2 Concept Design |  | To allow for an appropriate level of comparability, there must be a level of consistency in the WLC assessment approach. Require all sub-elements listed in the ‘COMPONENTS’ table below to be included in the LCA study, where present in the development. COMPONENTS TABLE INSERT HERE– RICS New Rules of Measurement (NRM) classification system Consider all life cycle stages relevant to the development in the LCA study, as defined by BS EN 15978 and these must be comparable for each iteration of the assessment. Present information for ‘Supplementary module D’ separately and consider and structure this around the circular economy principles. BS EN 15978 DIAGRAM INSERT HERE Present results in a consistent format e.g. kg of CO2 equivalent (CO2e) over 100 years. | Availability of operational templates; Detailed passive design analysis; Detailed dynamic simulation modelling; Demand response and renewables strategy. detailed approach within guide
Final OBC Early FBC | 3 Spatial Coordination |  |  | Client DSM walkthrough and sign-off: -Min. design perf. measures and EUI -Operational assumptions -Internal environmental conditions -Metering, programme and control
Performance review - pre-planning |  |  | Internal approval - Complete evaluation matrix and report on net zero aspirations and EUI predictions.
Final FBC | 4 Technical Design |  |  | Approve any changes before construction; Plan for inspection - build and commissioning - who, how and when?
Performance review - pre-construction |  |  | Internal approval - Update evaluation matrix and report any changes.
Construction & Commissioning | 5 Manufacture & Construction |  |  | Quality assurance: -Change control procedure - client sign-off -Inspection - client reports -Programme of physical testing - fabric integrity / air-quality
Project Monitoring & Evaluation | 6 Handover |  |  | EPC - Net Zero Carbon 'as-built'; Client in receipt of multi-disciplinary model (to support asset management, maintenance, in-use, adaptation).
Performance verification - 'as built' / pre-occupation |  |  | Internal approval - Update evaluation matrix and report any changes. Copy of the 'as built' EPC Confirmation of the 'as built' operational performance predictions - net zero and EUI
Project Monitoring & Evaluation | 7 |  |  | FM contracts, performance outcomes based on energy consumption; Model based performance analysis; Extended POE; Data disclosure.
Yes
No
N/A
Performance verification - in-use |  |  | Internal approval - Completed POE reporting template
Resources | UKGBC Net Zero Carbon Buildings: A Framework Definition; Climate Change (Emissions Reduction Targets) (Scotland) Act 2019

## Sheet2 (hidden)
Thermal Energy Demand Intensity (TEDI) is a measure of the building’s annual heating requirement; a metric that is primarily influenced by how well insulated and airtight a building is and by the ventilation system. For example, a highly insulated, airtight building with heat recovery ventilation will achieve a better TEDI value.
Initial Agreement Initial Design Statement | 1 Preparation and Briefing | The Energy Use Intensity (EUI) is a measure of the total energy consumed in a building annually; a metric that is solely dependent on how well the building will perform in-use, measured in kWh/m2.yr. An EUI includes all regulated and unregulated energy consumption. EUI Inform an EUI benchmark that can be specified in the brief and utilised during early design stages. Utilise existing data on the NHSS energy monitoring and targeting site, identifying best practice projects where possible, to inform the EUI. The building’s energy demand for space heating and cooling can be significantly reduced through enhanced fabric performance and passive design measures. Performance measures should be specified within the brief to encourage design development that promotes a fabric first approach. Space heating Reduce space heating demand. Adopt a passive design target of <15 kWh/m2.yr or utilise existing data on the NHSS energy monitoring and targeting site, identifying best practice projects where possible, to inform the benchmark. Fabric performance Require the specification of highly efficient fabric and external shading design to reduce the heating and cooling demand. Promote passive design and fabric efficiency by requiring the following indicative fabric performance measures: Walls <0.15 W/m2K Windows <1.0 W/m2K Floor <0.12 W/m2K Doors <1.2 W/m2K G-value of glass <1.2 W/m2K Roof <0.12 W/m2K Air permeability <1 m3/h.m2@50Pa Thermal bridges can account for considerable heat loss in a building and as buildings become better insulated this becomes even more significant. Thermal bridges can create localised cold-spots, leading to condensation build-up or mould growth. Losses are calculated by considering junction PSI-values and a building’s y-value. The lower the U-values, Y-values and PSI-values, the lower the fabric heat loss. Thermal bridge losses Limit the overall heat loss arising from thermal bridge losses by setting a maximum y-value of 0.04 W/m2K. Request that junction PSI-values, for each of the junctions where the building elements meet, are quantified and improved where possible. Prior to optimising building systems’ to satisfy predicted consumption levels, energy demand should first be limited, as far as reasonably possible, through the building fabric and passive measures. To further increase the overall efficiency of the building in-use, the specification of energy efficient building systems and the integration of smart energy management systems are required. Improvements should include highly energy efficient HVAC, lighting and vertical transport systems as well as the integration of intuitive and responsive building management systems. Designs should take account of recommended heating and hot water coefficients of performance (COP) and Seasonal Performance Factors. The physical wellbeing of building occupants should be considered alongside energy reductions. These include considerations around indoor air quality, daylight and overheating. Further guidance is included within the Wellbeing section of this document. System efficiency measures Reference trusted sources when considering setting limits for lighting power density, e.g. EU Green Public Procurement Indoor Lighting Technical Background Report where normalised lighting power density for hospital wards and examination rooms is recommended as 3.5 – 4 W/m2/100lux. Require the specification of heat pumps with a Seasonal Coefficient of Performance of 2.8 or above, where the COP for GSHPs is over 4 and ASHPs is over 3. Where Mechanical Ventilation is deemed the most suitable system, Mechanical Ventilation with Heat Recovery (MVHR) with an efficiency of at least 90% is required. Energy efficient solutions are required to be specified for any vertical transport systems, with the number and size dictated by demand and usage patterns. The use of regenerative drives should be considered and energy efficient features should be specified for lighting, standby options and VVF control of the drive motor. BEMS, metering, control and programming ……..