## Introduction & Overview
V1 - August 2025
SDaC Evaluation Tool
Introduction and Overview
Background: SHTN 02-01: the Sustainable Design and Construction(SDaC) Guide has been developed by NHSScotland in response to Scottish Government’s climate emergency declarations and related national commitments set out in DL (2021) 38. It details the process, actions and additional supporting standards required for NHS boards to evidence and deliver the performance outcomes needed to mitigate the health impacts of climate change and achieve sustainable quality in the present and future delivery of the healthcare built environment across Scotland. The Sustainable Design and Construction (SDaC) Evaluation Toolkit is designed to complement this guidance. It provides a framework for NHS boards to ensure that they use all necessary methodologies and tools and understand good practice approaches to allow them to meet policy requirements that will deliver a robust, sustainable healthcare environment. The Toolkit should be used by NHS boards to demonstrate their decision-making process when implementing the SDaC framework. The SDaC Evaluation Toolkit is designed to be applied throughout the project lifecycle from strategic definition, preparation and briefing, through to handover and in use (Royal Institute British Architects (RIBA) stages 0 through 7) and has defined reporting stages to align with project development. It should be used both as a self-assessment tool and for formal governance reporting purposes including for capital Investment projects where third party assessment is provided by NHSScotland Assure.
Completion: The Evaluation Toolkit should be completed by the project lead or sustainability champion as part of their record of sustainable self-assessment and decision making. The toolkit is designed to be used as a working tool to be completed through each project stage and ensure necessary criteria and actions are competed and recorded. Teams should record responsibility and due dates for evidence as well as keep notes on current actions and recorded evidence. Evidence should be stored alongside this tool or even embedded within the tool itself as pdf, excel or word documents – refer examples below. NHS boards should ensure that evidence is specific and related directly to the expected evidence criteria, the notes column should be used to help provide a narrative to this. Where evidence relies upon completion of design tool information, such as Dynamic Simulation Modelling, Whole Life Carbon Assessments, Thermal Bridging calculations and so on it is recommended that third party assessment is undertaken to verify results. This will be a requirement where projects are supported through NHSScotland Assure. It is recommended that recording of a completed stage forms part of project governance.
Scope: For projects where certain criteria will be dependant on the scope of works (please refer to figure 0.1 within the guidance document) it is recommended that the Board evidence where criteria are not applicable by recording a confirmation statement that explains their decision making. Once this is completed users should mark those areas as N/A on a statement by statement basis to ensure summary reporting within the dashboard remains accurate.
Additional Support: NHSScotland Assure are available to support Boards with the application of SHTN 02-01 and the use of this evaluation tool. The NHSScotland Assure team can also provide independent assessment of the completion of the evaluation tool to support investment or governance processes mandated by Scottish Government, or by request.
As noted above, the process adheres to the industry standard Royal Institute of British Architects (RIBA) Plan of Work stages. For more information please click here.
Example: Below is an example of what a completed report might start to look like, including self, evidence, self assessment scoring and where applicable additional notes:

## Project Information & Dashboard
SDaC Evaluation Tool
Project Information and Dashboard
| Board: | Select from Dropdown…
| Project Title: | Example Project
| NHS Project Lead: | Example Name - complete cell D9
| Sustainability Champion: | Example Name - complete cell D11
| Project Description: | Please complete a short project description, this should cover the services affected, planned initial scope of the project and key driver for change. Approx 150 words.
| Current RIBA Stage: | Select from Dropdown…
Project Team
| Role | Name | Organisation
| NHS Project Lead | Example Name - complete cell D9
| Sustainability Champion | Example Name - complete cell D11
FM Lead
Procurement Team
Capital Planning Lead
Estates Lead
Digital Lead
…and so on.

## RIBA Stage 0
SDaC Evaluation Tool
Select from Dropdown…: Example Project
RIBA Stage 0 Evaluation
| Priority Theme / Sub Theme | Evaluation Criteria | Required Data Validation | Expected Evidence | Due Date | Responsible Party | Evidence/ Reporting | Evaluation Assessment | Notes
| Wellbeing / Social Wellbeing | Include the requirements of Social Wellbeing (ref 3.13) within early decision making relating to the scope of the project, particularly related to community wealth building opportunities | N/A | •Evidence of discussions with local authority partners/ public sector partners/ community groups/ organisations on the alignment of service provisions and potential for partnership/ inclusion within project scope. •Evidence that Place Principles have been considered when defining the scope of the project. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Conservation | Include the requirements of Energy Conservation (ref 4.5-4.40) within early decision making | N/A | •Evidence of Space Utilisation analysis, including engagement with stakeholders, occupancy use data analytics based on real time usage information, space audits, departmental flow pathway analysis and so on. •Evidence of Space Utilisation analysis having informed clinical brief and initial SoA, including rationalisation based on occupancy usages and clinical pathways. •Evidence of the consideration of digital health solutions within the clinical briefing, including opportunities for mobile services. •Evidence that a structural assessment has taken place to inform decision making and prioritise refurbishment and deep retrofit. •Evidence that strategic decision making has followed a refurbishment, retrofit, brownfield, greenfield sequential optioneering approach as per site selection criteria (ref 5.3-5.9). •Evidence that work has been undertaken to determine a list of all relevant statutory compliance and Guidance required. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Efficiency | Include the requirements of Energy Efficiency (ref 4.41-4.68) within early decision making | N/A | •Evidence that energy audits to identify opportunities for optimisation and implement measures to enhance the efficiency of existing systems have been undertaken and helped to inform project scope. |  |  |  | Not Yet Evidenced

## RIBA Stage 1
SDaC Evaluation Tool
Select from Dropdown…: Example Project
RIBA Stage 1 Evaluation
| Priority Theme / Sub Theme | Evaluation Criteria | Required Data Validation | Expected Evidence | Due Date | Responsible Party | Evidence / Reporting | Evaluation Assessment | Notes
| Wellbeing / Social Wellbeing | Include the requirements of Social Wellbeing (ref 3.8-3.13) within the SoA and Brief | Expected quantity of space which will be available for social use (% of development and m2) | •Evidence of requirement for spaces, including greenspace, which can contribute and/ or are focussed on social wellbeing within the outline SoA. •Briefing on the flexibility of spaces to allow social use. •High level outline briefing on wayfinding. |  |  |  | Not Yet Evidenced
| Wellbeing / Physical Wellbeing | Include the requirements of Physical Wellbeing (ref 3.20-3.28) within the SoA and Brief | Briefed thermal comfort and overheating data (all three criteria indicate a pass - ref 6.6) | •Briefing to include the requirements of physical wellbeing. •Evidence that the requirement for appropriate DSM has been included in the brief/ project scope, including TM52/ 49, thermal comfort modelling and where relevant TM59. |  |  |  | Not Yet Evidenced
| Wellbeing / Occupational Wellbeing | Include the requirements of Occupational Wellbeing (ref 3.29-3.34) within the SoA and Brief | N/A | •Briefing to include the requirements of Occupational Wellbeing. |  |  |  | Not Yet Evidenced
| Wellbeing / Economic Wellbeing | Include the requirements of Economic Wellbeing (ref 3.35-3.43) within the SoA and Brief | N/A | •Evidence where within the SoA spaces have been highlighted as multi functional. •Evidence that Brief calls for consideration of economic wellbeing requirements, for example use of MMC, BIM, adaptable/ flexible spaces, passive design approaches, lifecycle costing and so on. |  |  |  | Not Yet Evidenced
| Wellbeing / Mental Wellbeing | Include the requirements of Mental Wellbeing (ref 3.14-3.19) within the Brief | N/A | •Briefing to include the requirements of mental wellbeing. •Evidence that the requirement for CBDM has been included in the brief/ project scope including briefing requirements of appropriate natural light levels. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Conservation | Include the requirements of Energy Conservation (ref 4.5-4.40) within the SoA and Brief | •Briefed Building Fabric Data (meet or exceed table 4.1): •U-Values & G-Values Targets •Air Permeability Targets •Thermal Bridge Target •Form Factor Target (<3) •WLCA: Upfront Carbon Targets (meet or exceed table 4.2) | •Evidence that departmental pathway analysis, digital healthcare solutions and space optimisation plan have been used to inform brief, SoA and adjacencies. •Evidence that the brief calls for compliance with all relevant statutory and NHSScotland technical guidance as well as Board and Scottish Government policy. •Evidence that the Brief and SOA include requirements of energy conservation, multifunctional spaces, efficient storage solutions and digital storage, the need to preserve historic elements of infrastructure (ref 4.22), energy efficient systems and so on. •Evidence that a fabric first approach has been instilled within the brief and design, highlighting requirements for thermal bridging, u-values, low carbon materials, airtightness, form factor, orientation, glazing ratios, shading and thermal mass |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Efficiency | Include the requirements of Energy Efficiency (ref 4.41-4.68) within the SoA and Brief | Briefed Operational Energy Data (meet or exceed table 4.3, or provide bespoke EUI through NHS England Calculation (ref 5.2-5.21) | •Evidence that the brief calls for compliance with all relevant statutory and NHSScotland technical guidance as well as Board and Scottish Government policy. •Briefing to include the requirements of Energy Efficiency, evidence that the brief calls for energy-efficient systems and high-performance fabric elements to improve thermal performance, as well as centralised control for example, integrated HVAC, lighting, security, and other systems for coordinated operation and use BMS to ensure systems work together efficiently and effectively and can be monitored and adjusted for optimal performance. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Renewable, Sustainable Energy Sources | Include the requirements of Renewable, Sustainable Energy Sources (ref 4.69-4.82) within the SoA and Brief | N/A | •Evidence that the brief calls for sustainable energy sources to be integrated and for the project to be designed for future integration. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Insetting | Include the requirements of Insetting (ref 4.83-4.88) within the SoA and Brief | N/A | •Evidence that the brief calls for consideration of insetting opportunities, for example biochar, green roofs/ walls and so on as well as efficient construction practices and techniques that minimise waste and reduce energy consumption, such as modular construction and prefabrication. |  |  |  | Not Yet Evidenced

## RIBA Stage 2
SDaC Evaluation Tool
Select from Dropdown…: Example Project
RIBA Stage 2 Evaluation
| Priority Theme / Sub Theme | Evaluation Criteria | Required Data Validation | Expected Evidence | Due Date | Responsible Party | Evidence / Reporting | Evaluation Assessment | Notes
| Wellbeing / Social Wellbeing | Include the requirements of Social Wellbeing (ref 3.8-3.13) within the concept design and option appraisal criteria | Expected quantity of space which will be available for social use (% of development and m2) . | •Evidence that social connectivity and the place principles have been utilised as part of option appraisal scoring. •Evidence of brief development including social wellbeing criteria. •Clear evidence from sketch proposals of the inclusion of spaces for social wellbeing. |  |  |  | Not Yet Evidenced
| Wellbeing / Mental Wellbeing | Include the requirements of Mental Wellbeing(ref 3.14-3.19) within the concept design and option appraisal criteria - for example adequate greenspace | Green Space Factor >0.4 confirmation OR confirmation of Biodiversity Net Gain | •Evidence that greenspace/ biodiversity have been included as part of option appraisal scoring. •Clear evidence from sketch proposals of the inclusion of spaces for mental wellbeing. |  |  |  | Not Yet Evidenced
| Wellbeing / Physical Wellbeing | Include the requirements of Physical Wellbeing (ref 3.20-3.28) within the concept design and option appraisal criteria | N/A | •Evidence that active travel and flood risk requirements have been included as part of option appraisal scoring. •Clear evidence from sketch proposals of the inclusion of spaces for physical wellbeing. |  |  |  | Not Yet Evidenced
| Wellbeing / Occupational Wellbeing | Include the requirements of Occupational Wellbeing (ref 3.29-3.34) within the concept design and option appraisal criteria | N/A | N/A |  |  |  | Not Yet Evidenced
| Wellbeing / Economic Wellbeing | Include the requirements of Economic Wellbeing (ref 3.35-3.43) within the concept design and option appraisal criteria | N/A | •Evidence that economic Wellbeing factors have been utilised as part of option appraisal scoring, for example capacity for onsite renewables and so on. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Conservation | Include the requirements of Energy Conservation (ref 4.5-4.40) within the concept design and option appraisal criteria | •Form Factor Target (Based on Preferred Option) | •Evidence that the option appraisal scoring takes account of the refurbishment, retrofit, brownfield, greenfield sequential approach to development. (ref5.3-5.9). •Evidence that a fabric first approach has been included as part of option appraisal scoring, including elements such as form factor and orientation. •Clear evidence from sketch proposals of energy conservation requirements, form factor, orientation and so on. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Efficiency | Include the requirements of Energy Efficiency (ref 4.41-4.68) within the concept design and option appraisal criteria | N/A | •Evidence that Energy Efficiency is a key component of options appraisals for maintenance only projects. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Renewable, Sustainable Energy Sources | Include the requirements of Renewable, Sustainable Energy Sources (ref 4.69-4.82) within the concept design and option appraisal criteria | N/A | •Evidence solar/ wind/ geothermal energy feasibility studies to help inform site appraisal scoring. •Demonstrate consideration of modular systems such as modular HVAC and energy systems that can be easily expanded and upgraded and use prefabricated components for flexibility. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Insetting | Include the requirements of Insetting (ref 4.83-4.88) within the concept design and option appraisal criteria | N/A | •Clear evidence of a developed plan to integrate carbon insetting measures during the design and construction stage. |  |  |  | Not Yet Evidenced

## RIBA Stage 3
0
SDaC Evaluation Tool
Select from Dropdown…: Example Project
RIBA Stage 3 Evaluation
| Priority Theme / Sub Theme | Evaluation Criteria | Required Data Validation | Expected Evidence | Due Date | Responsible Party | Evidence / Reporting | Evaluation Assessment | Notes
| Wellbeing / Physical Wellbeing | Include the requirements of Physical Wellbeing (ref 3.20-3.28) within the outline design | DSM modelling with as expected thermal comfort and overheating data(all three criteria indicate a pass - ref 6.6) | •Evidence of a design which provides accessible circulation routes, direct access to greenspace, flexible furniture and layouts (plans and spec), security/surveillance and controlled access, for example 1:50 Plans, GA Plans, Specifications and so on •Evidence of specifications meeting briefing requirements regarding VOC's and non toxic materials, accessible controls for temp/lighting and so on •Detailed DSM information: Thermal comfort modelling , TM52/ 59 and 49 •Evidence of an environmental security approach towards flooding / overheating |  |  |  | Not Yet Evidenced
| Wellbeing / Occupational Wellbeing | Include the requirements of Occupational Wellbeing (ref 3.29-3.34) within the detailed design | N/A | •Evidence of spaces, including greenspace, which can contribute and/ or are focussed on Occupational Wellbeing, 1:50 PLANS/ GA Plans , for example, functional staff areas, storage spaces, respite for staff, changing facilities, staff lounges, quiet rooms, break rooms, training spaces and so on. •Evidence of specifications meeting the requirements of occupational wellbeing, for example fixed and mobile furniture, furniture types, digital tools and technology and so on. •Evidence of a clear and appropriate professional development strategy, linked with building spaces, for example clinical pathways with appropriate training space/ opportunities for staff development. |  |  |  | Not Yet Evidenced
| Wellbeing / Economic Wellbeing | Include the requirements of Economic Wellbeing(ref 3.35-3.43) within the developed design | N/A | •Evidence of spaces, including greenspace, which can contribute to economic wellbeing, SoA, 1:50 PLANS / GA Plans indicating efficient use of space, multi functional space, adaptation/ expansion plans, flexibility of spaces, and passive design approaches for example. •Evidence of specifications meeting the requirements of economic wellbeing, for example smart building management, renewable onsite energy sources, durable materials, fabric first approach. |  |  |  | Not Yet Evidenced
| Wellbeing / Social Wellbeing | Include the requirements of Social Wellbeing(ref 3.8-3.13) within the outline design | Expected quantity of space which will be available for social use (% of development and m2) . | •Evidence of spaces, including greenspace, which can contribute to and/ or are focussed on social wellbeing, 1:50 PLANS / GA Plans, SoA. •Evidence of clear and appropriate wayfinding strategy. •Evidence of local supplier/ contractor discussions/ appointments. •Evidence of discussions with local community groups/ organisations on provision of services/ spaces and so on. |  |  |  | Not Yet Evidenced
| Wellbeing / Mental Wellbeing | Include the requirements of Mental Wellbeing(ref 3.14-3.19) within the outline detailed design | Green Space Factor >0.4 confirmation OR Confirmation of Biodiversity Net Gain CBDM Outputs indicating provision of good quality natural light between 300-3000lux for occupied spaces, including compliance with CIBSE LG2:Lighting in Healthcare premises | •Evidence of spaces, including greenspace, which can contribute to and/ or are focussed on mental wellbeing, 1:50 PLANS/ GA Plans. •Evidence of clear and appropriate wayfinding strategy and arts strategy. •CBDM evidence which shows spaces meet required visual comfort levels. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Conservation | Include the requirements of Energy Conservation (ref 4.5-4.40) within the detailed design | •Expected Building Fabric Data (meet or exceed table 4.1): •U-Values & G-Values Targets •Air Permeability Targets •Thermal Bridge Target •Form Factor as designed (meet or exceed <3) •WLCA: •Upfront Carbon Targets (meet or exceed table 4.2) •Overall WLCA Target | •Evidence of necessary statutory authority approvals. •Evidence of plans for booking systems for shared spaces - ensure technology integrated as required. •Evidence of specifications meeting the requirements of a fabric first approach, for example thermal bridging, u-values, low carbon materials, airtightness, shading and thermal mass, passive cooling, nature based solutions. •Evidence of design and spaces, including greenspace, which can contribute to and/ or are focussed on Energy Conservation, 1:50 PLANS/ GA Plans indicating orientation, form factor delivery, glazing ratios, spaces for digital healthcare solutions, multifunctional spaces/ flexible spaces - including modular furniture/ moveable partitions and so on. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Efficiency | Include the requirements of Energy Efficiency(ref 4.41-4.68) within the detailed design | TM54 DSM with Expected Operational Energy Data (meet or exceed targets set during RIBA Stage 1) | •Evidence of statutory and NHSScotland technical compliance. •Demonstrate that NHS boards have chosen systems which are highly energy efficient and implement programmable thermostats, zone control, occupancy detection to control heating and cooling based on need to be as efficient as practicable. This should include energy-efficient lighting and appliances - install LED lighting and energy-efficient appliances and equipment to reduce electricity consumption. GA Plans, schematics, specifications and so on. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Renewable, Sustainable Energy Sources | Include the requirements of Renewable, Sustainable Energy Sources (ref 4.69-4.82) within the detailed design | N/A | •Evidence flexible infrastructure design which allows for future renewable energy source integration. •Evidence space allocation for proposed or future renewable, sustainable energy source integrations. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Insetting | Include the requirements of Insetting (ref 4.83-4.88) within the detailed design | N/A | •Evidence that specification incorporates materials that store carbon, such as wood and bio-based insulation. •Evidence of spaces or systems incorporated into the design as part of carbon insetting measures. GA plans, 1:50 plans, specifications. |  |  |  | Not Yet Evidenced

## RIBA Stage 4
SDaC Evaluation Tool
Select from Dropdown…: Example Project
RIBA Stage 4 Evaluation
| Priority Theme / Sub Theme | Evaluation Criteria | Required Data Validation | Expected Evidence | Due Date | Responsible Party | Evidence / Reporting | Evaluation Assessment | Notes
| Wellbeing / Mental Wellbeing | Include the requirements of Mental Wellbeing (ref 3.14-3.19) within the detailed design | Green Space Factor >0.4 confirmation OR confirmation of Biodiversity Net Gain CBDM Outputs indicating provision of good quality natural light between 300-3000 lux for occupied spaces, including compliance with CIBSE LG2:Lighting in Healthcare premises | •Evidence of spaces, including greenspace, which can contribute and/or are focussed on mental wellbeing, 1:50 PLANS / GA Plans. •Evidence of clear and appropriate wayfinding strategy and arts strategy. •CBDM evidence which shows spaces meet required visual comfort levels. |  |  |  | Not Yet Evidenced
| Wellbeing / Physical Wellbeing | Include the requirements of Physical Wellbeing (ref 3.20-3.28) within the detailed design | DSM modelling with as designed thermal comfort and overheating data (all three criteria indicate a pass - ref 6.6) | •Evidence of a design which provides accessible circulation routes, direct access to greenspace, flexible furniture and layouts (plans and specification), security/ surveillance and controlled access, for example 1:50 Plans, GA Plans, specifications and so on. •Evidence of specifications meeting briefing requirements regarding VOC's and non toxic materials, accessible controls for temperature/ lighting and so on. •Detailed DSM information: Thermal comfort modelling , TM52/ 59 and 49. •Evidence of an environmental security approach towards flooding / overheating. |  |  |  | Not Yet Evidenced
| Wellbeing / Occupational Wellbeing | Include the requirements of Occupational Wellbeing (ref 3.29-3.34) within the detailed design | N/A | •Evidence of spaces, including greenspace, which can contribute to and/ or are focussed on Occupational Wellbeing,1:50 PLANS/ GA Plans, for example, functional staff areas, storage spaces, respite for staff, changing facilities, staff lounges, quiet rooms, break rooms, training spaces and so on. •Evidence of specifications meeting the requirements of Occupational Wellbeing, for example fixed and mobile furniture, furniture types, digital tools, technology and so on. •Evidence of clear and appropriate professional development strategy, linked with building spaces, for example clinical pathways with appropriate training space/ opportunities for staff development. |  |  |  | Not Yet Evidenced
| Wellbeing / Economic Wellbeing | Include the requirements of Economic Wellbeing (ref 3.35-3.43) within the detailed design | N/A | •Evidence of spaces, including greenspace, which can contribute to economic wellbeing, SoA, 1:50 PLANS/ GA Plans indicating efficient use of space, multi functional space, adaptation/ expansion plans, flexibility of spaces, and passive design approaches for example. •Evidence of specifications meeting the requirements of economic wellbeing, for example smart building management, renewable onsite energy sources, durable materials, fabric first approach. •Evidence of clear and appropriate maintenance strategy. |  |  |  | Not Yet Evidenced
| Wellbeing / Social Wellbeing | Include the requirements of Social Wellbeing (ref 3.8-3.13) within the detailed design | Expected quantity of space which will be available for social use (% of development and m2) | •Evidence of spaces, including greenspace, which can contribute and/or are focussed on social wellbeing, 1:50 PLANS / GA Plans , SoA, •Evidence of clear and appropriate wayfinding strategy. •Evidence of local supplier/contractor discussions/appointments. •Evidence of discussions with local community groups/organisations on provision of services/spaces and so on. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Conservation | Include the requirements of Energy Conservation (ref 4.5-4.40) within the detailed design | •Designed Building Fabric Data (meet or exceed table 4.1): •U-Values & G-Values as designed •Air Permeability as designed •Thermal Bridge as designed •Form Factor as designed (<3) •WLCA: •Upfront Carbon as designed (meet or exceed table 4.2) •Overall WLCA as designed | •Evidence of necessary statutory authority approvals. •Detailed evidence of plans for booking systems for shared spaces - ensure technology is integrated as required. • Detailed evidence of specifications meeting the requirements of a fabric first approach, for example thermal bridging, u-values, low carbon materials, airtightness, shading and thermal mass, passive cooling, nature based solutions •Detailed evidence of design and spaces, including greenspace, which can contribute and/ or are focussed on Energy Conservation, 1:50 PLANS/ GA Plans indicating orientation, form factor delivery, glazing ratios, spaces for digital healthcare solutions, multifunctional spaces /flexible spaces - including modular furniture/ moveable partitions and so on. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Efficiency | Include the requirements of Energy Efficiency (ref 4.41-4.68) within the detailed design | TM54 DSM with Designed Operational Energy Data (meet or exceed targets set during RIBA Stage 3) | •Evidence of statutory and NHSScotland technical compliance. •Demonstrate that NHS boards have chosen systems which are highly energy efficient and implement programmable thermostats, zone control, occupancy detection to control heating and cooling based on need to be as efficient as practicable. This should include energy-efficient lighting and appliances - install LED lighting and energy-efficient appliances and equipment to reduce electricity consumption. GA Plans, schematics, specifications and so on. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Renewable, Sustainable Energy Sources | Include the requirements of Renewable, Sustainable Energy Sources (ref 4.69-4.82) within the detailed design | N/A | •Evidence that the design of electrical and mechanical systems is flexible to allow for future integration of renewable energy technologies and that conduit and piping systems can accommodate additional wiring and plumbing for future upgrades. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Insetting | Include the requirements of Insetting (ref 4.83-4.88) within the detailed design | N/A | •Evidence that specification incorporates materials that store carbon, such as wood and bio-based insulation. •Evidence of spaces or systems incorporated into the design as part of carbon insetting measures, GA plans, 1:50 plans, specifications. |  |  |  | Not Yet Evidenced

## RIBA Stage 5
SDaC Evaluation Tool
Select from Dropdown…: Example Project
RIBA Stage 5 Evaluation
| Priority Theme / Sub Theme | Evaluation Criteria | Required Data Validation | Expected Evidence | Due Date | Responsible Party | Evidence / Reporting | Evaluation Assessment | Notes
| General | Ensure that the SDaC is considered throughout the construction period | N/A | •Evidence that change control processes consider the requirements of SDaC as part of decision making. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Conservation | Include the requirements of Energy Conservation (ref 4.5-4.40) within the construction stage | •Constructed Building Fabric Data (meet or exceed table 4.1): •U-Values & G-Values as constructed •Air Permeability as constructed •Thermal Bridge as constructed •Form Factor as constructed (<3) •WLCA: •Upfront Carbon as constructed (meet or exceed table 4.2) •Overall WLCA as constructed | •Evidence that design plans and specifications have met the brief. •Evidence high quality and meticulous construction practices which ensure the designed fabric first approach is delivered, for example airtightness: use airtight membranes and tapes to seal gaps, penetrations and joints. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Efficiency | Include the requirements of Energy Efficiency(ref 4.41-4.68) within the construction stage | TM54 DSM with Constructed Operational Energy Data (meet or exceed targets set during RIBA Stage 4) | •Evidence that tests have been carried out to verify that systems are installed and operating correctly and that any deficiencies are identified and addressed to ensure optimal performance and energy consumption. •Evidence a plan that outlines the commissioning process for all building systems, including implementation and management of seasonal commissioning as well as the transition period from commissioning to handover and operation. The plan must include pre-functional checklists, functional performance tests, and system verification. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Insetting | Include the requirements of Insetting (ref 4.83-4.88) within the construction stage |  | •Implement efficient construction practices and techniques that minimise waste and reduce energy consumption, such as modular construction and prefabrication. |  |  |  | Not Yet Evidenced

## RIBA Stage 6&7
SDaC Evaluation Tool
Select from Dropdown…: Example Project
RIBA Stage 6&7 Evaluation
| Priority Theme / Sub Theme | Evaluation Criteria | Required Data Validation | Expected Evidence | Due Date | Responsible Party | Evidence / Reporting | Evaluation Assessment | Notes
| Wellbeing / Social Wellbeing | Include the requirements of Social Wellbeing (ref 3.8-3.13) within the delivered design and PoE assessments | Quantity of space which will be available for social use (% of development and m2) | •Final marked up plans/ photographs of spaces, wayfinding delivered. •Final summary of engagement which took place with local community groups/ organisations, evidence of anticipated use in place. •Final summary of appointed local suppliers/contractors. |  |  |  | Not Yet Evidenced
| Wellbeing / Mental Wellbeing | Include the requirements of Mental Wellbeing (ref 3.8-3.13) within the delivered design and PoE assessments | Green Space Factor >0.4 confirmation OR Confirmation of Biodiversity Net Gain | •Final marked up plans/ photographs of spaces (including greenspace), wayfinding and arts strategy delivered. •Final evidence of as constructed GSF/ Biodiversity Net Gain. •Final CBDM evidence indicating compliant as constructed design. |  |  |  | Not Yet Evidenced
| Wellbeing / Physical Wellbeing | Include the requirements of Physical Wellbeing (ref 3.20-3.28) within the delivered design and PoE assessments | DSM modelling with as constructed thermal comfort and overheating data (all three criteria indicate a pass - ref 6.6) | •Final marked up plans/ photographs of spaces (including greenspace), flexible furniture, accessible controls and so on. •Final evidence of as constructed DSM modelling. |  |  |  | Not Yet Evidenced
| Wellbeing / Occupational Wellbeing | Include the requirements of Occupational Wellbeing (ref 3.29-3.34) within the delivered design and PoE assessments | N/A | •Final marked up plans/ photographs of spaces (including greenspace),conducive to occupational wellbeing. •Final evidence of how the building will contribute to professional development. |  |  |  | Not Yet Evidenced
| Wellbeing / Economic Wellbeing | Include the requirements of Economic Wellbeing (ref 3.35-3.43) within the delivered design and PoE assessments | N/A | •Final marked up plans/ photographs of spaces (including greenspace),conducive to the principles of economic wellbeing, for example flexible/ multifunctional spaces. •Final evidence of as constructed adaptation/ expansion plans and maintenance strategy. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Conservation | Include the requirements of Energy Conservation (ref 4.5-4.40) within the delivered design and PoE assessments | N/A | •Final marked up plans/ photographs of spaces (including greenspace),conducive to energy conservation. •Final evidence of as constructed specifications. |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Energy Efficiency | Include the requirements of Energy Efficiency(ref 4.41-4.68) within the delivered design and PoE assessments | •Benchmarking: Compare the collected data against the TM54 predictions to identify discrepancies and areas for improvement. | •Final marked up plans/ photographs of spaces/systems, conducive to Energy Efficiency. •Evidence robust maintenance and operation plans to demonstrate efficiency and longevity are maximised. •Confirm that BMS is used to track energy consumption and identify areas for improvement and implement energy-saving measures based on monitoring data to optimise energy consumption. •Evidence use of use occupancy sensors to control lighting and HVAC systems based on real-time usage as well as implementing daylight sensors to adjust artificial lighting based on natural light availability. •Evidence of integration of automated controls to optimise energy use and reduce waste and use BMS to coordinate and control building systems. • Identify any differences between predicted and actual energy use, and find causes of these differences through TM61 |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Renewable, Sustainable Energy Sources | Include the requirements of Renewable, Sustainable Energy Sources (ref 4.69-4.82) within the delivered design and PoE assessments | N/A | •Final marked up plans/photographs of renewable, sustainable energy sources requirements incorporated into the scheme |  |  |  | Not Yet Evidenced
| Energy Hierarchy / Insetting | Include the requirements of Insetting (ref 4.83-4.88) within the delivered design and PoE assessments | N/A | •Evidence that as part of PoE and ongoing maintenance/ management the NHS board will: •regularly track emissions and ongoing carbon sequestration within the building and site • conduct regular assessments to verify the effectiveness of carbon insetting measures and make necessary adjustments • ensure that carbon sequestration measures, such as biochar and green roofs, are maintained and monitored for long-term effectiveness. |  |  |  | Not Yet Evidenced

## Data Validation (hidden)
Select from Dropdown… | Select from Dropdown…
NHS Ayrshire and Arran | Stage 0: Strategic Definition | Wellbeing / Social Wellbeing | Not Yet Evidenced | NHS Project Lead: Example Name - complete cell D9,
NHS Borders | Stage 1: Preparation & Briefing | Wellbeing / Mental Wellbeing | N/A - Not Applicable | Sustainability Champion: Example Name - complete cell D11,
NHS Dumfries and Galloway | Stage 2: Concept Design | Wellbeing / Physical Wellbeing | Criteria Exceeded | FM Lead : ,
NHS Fife | Stage 3: Spatial Coordination | Wellbeing / Occupational Wellbeing | Fully Evidenced | Procurement Team: ,
NHS Forth Valley | Stage 4: Technical Design | Wellbeing / Economic Wellbeing | Partially Evidenced | Capital Planning Lead: ,
NHS Grampian | Stage 5: Manufacturing & Construction | Energy Hierarchy / Energy Conservation | Criteria Not Met | Estates Lead: ,
NHS Greater Glasgow and Clyde | Stage 6: Handover | Energy Hierarchy / Energy Efficiency |  | Digital Lead : ,
NHS Highland | Stage 7: In Use | Energy Hierarchy / Renewable, Sustainable Energy Sources |  | …and so on.: ,
NHS Lanarkshire |  | Energy Hierarchy / Insetting |  | : ,
NHS Lothian |  | General |  | : ,
NHS Orkney |  |  |  | : ,
NHS Shetland |  |  |  | : ,
NHS Tayside |  |  |  | : ,
NHS Western Isles |  |  |  | : ,
Healthcare Improvement Scotland |  |  |  | : ,
NHS 24 |  |  |  | : ,
Public Health Scotland |  |  |  | : ,
NHS National Services Scotland |  |  |  | : ,
NHS National Waiting Times Centre |  |  |  | : ,
Scottish Ambulance Service |  |  |  | : ,
State Hospitals Board for Scotland |  |  |  | : ,
NHS Education for Scotland |  |  |  | : ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,
: ,